## Version
Version History
Version | Date | Author | Comments | Known Issues
0.1 | 2019-08-09 | PY Lim | Issued for internal review.
1 | 2019-08-15 | J. Hamra | For Release
2 | 2021-08-27 | J. Hamra | Additional Instrument sheets added beyond VSD Datasheet tab
3 | 2024-11-29 | J. Hamra | Added H2S Sensor and HV Switchgear tabs

## How To Use
SA Water Datasheet Template Instructions
How to complete the Datasheet:
1. Enter project information in the top rows of the datasheet tab, and revision details in the bottom rows of the datasheet tab.
2. When entering data into the datasheet, make sure that the units of the quantities entered are correct. If changes are made to the units, highlight the cell in yellow to indicate this.
3. If the Client has not completed a specification entry, please ensure that the specification of what is being offered is included in the "Offered" column.
4. If a particular specification parameter is not applicable to the offer, please enter "N/A" in the "Offered" column of that row.
Troubleshooting
Contact the SA Water Principal Electrical Engineer for any issues regarding this datasheet template.

## INDEX
Datasheet (click to go to tab)
Site Locational Data
Control Equipment
Electric Motor
LV Switchboard
HV Switchgear
Misc Electrical Equipment
VSD Datasheet
Diesel Generator
Telemetry
Local Telemetry Bridge
Turbidity Analyser
Conductivity Analyser
pH Analyser
Flow Switch
Level Switch
Flowmeter
Pressure Transmitter
Hydrostatic Level Transmitter
Radar Level Transmitter
UV Disinfection System
Kiosk Substation
H2S Sensor
Battery Charger Systems

## Site Locational Data
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Site Locational Data
Number |  | Units | Specification | Offered | Additional Comments
1 | Site Location
1.1 | Site Name
1.2 | Site Address
1.3 | Site Location Coordinates
2 | Consumer Connection
2.1 | Meter Number
2.2 | Full Load Capacity | kW/kVA
2.3 | Minimum Power Factor (lead) | ratio
2.4 | Minimum Power Factor (lag) | ratio
2.5 | Rated Voltage | VAC | 400
2.6 | Rated Output Current | A
2.7 | Supply Continous Current | A
2.8 | Circuit Breaker or Fuse | Type
3 | Site Climatic Conditions
3.1 | Ambient temperature (min / max) | ºC | -5/50
3.2 | Ambient Air Temperature Yearly Average | °C
3.3 | Relative Humidity
3.4 | Pollution Degree
3.5 | Altitude | m
3.6 | Corrosive Environment (H2S/Marine) | Yes/No
4 | Pump
4.1 | Quantity
4.2 | Power | kW
4.3 | DOL, Soft Starter or VSD | Type
5 | Consumer Mains Cable
5.1 | Manufacturer
5.2 | Country of Manufacture
5.3 | Conductor Material | Cu/Al
5.4 | Insulation Material
5.5 | Conductor Size | mm2
5.6 | Single Core/Multicore
5.7 | Number in Parallel | Number of
6 | Generator Details
6.1 | Generator Power Rating | kVA
6.2 | Generator Configuration | Permanent/Temporary
Delivery / Lead Time
| Complete | Weeks |  |  | Maximum durations to be stated
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
LV Switchboard shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Control Equipment
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Control Equipment
Number |  | Units | Specification | Offered | Additional Comments
1 | Relays
1.1 | Manufacturer
1.2 | Equipment number / Model
1.3 | Coil Voltage | Vac/Vdc
1.4 | Contact Voltage | Vac/Vdc
2 | Push Buttons
2.1 | Manufacturer
2.2 | Equipment number / Model
2.3 | Diameter | mm
2.4 | Contact Voltage | Vac/Vdc
2.5 | Colour
2.6 | Front IP Rating
3 | Indicator Lamps
3.1 | Manufacturer
3.2 | Equipment number / Model
3.3 | Diameter | mm
3.4 | Incandescent / LED
3.5 | Colour
3.6 | Supply Voltage | Vac/Vdc
3.7 | Front IP Rating
4 | Surge Arresters
4.1 | Manufacturer
4.2 | Equipment number / Model
4.3 | Discharge Current | kA
4.4 | Rated Voltage | V ac
4.5 | Indicator Contact | Yes/No
4.6 | IP Rating
5 | Uninterruptible Power Supply (UPS)
5.1 | Manufacturer
5.2 | Equipment number / Model
5.3 | Output Voltage | V ac/V dc
5.4 | Output Current | A
5.5 | Battery Modules
6 | Power Meter
6.1 | Manufacturer
6.2 | Equipment number / Model
6.3 | Rated Voltage | V ac/V dc
6.4 | Accuracy Class
6.5 | Internal CT's | Yes/No
6.6 | Communication interface | Protocol (Ethernet, MODBUS, etc…)
7 | Emergency Stop Pushbuttons
7.1 | Manufacturer
7.2 | Equipment number / Model
7.3 | Diameter | mm
8 | Emergency Stop Relays
8.1 | Manufacturer
8.2 | Equipment number / Model
8.3 | SIL Rating
8.4 | Supply Voltage | Vac/Vdc
9 | Ventilation Fan
9.1 | Manufacturer
9.2 | Equipment number / Model
9.3 | Power Rating | kW
10 | Cubicle Heaters
10.1 | Manufacturer
10.2 | Equipment number / Model
10.3 | Power Rating | W
11 | PLC Central Processing Unit
11.1 | Manufacturer
11.2 | Equipment number / Model
11.3 | Supply Voltage | V ac/V dc
11.4 | Programming Software Type
11.5 | Number of Programming Software Copies | No.
12 | PLC I/O Modules
12.1 | Equipment number / Model
12.2 | Analogue Inputs | Number of
12.3 | Analogue Outputs | Number of
12.4 | Digital Inputs | Number of
12.5 | Digital Outputs | Number of
12.6 | Rated Voltage Digital Inputs | V ac/V dc
12.7 | Rated Current Digital Inputs | A
12.8 | Rated Voltage Digital Outputs | V ac/V dc
12.9 | Rated Current Digital Outputs | A
13 | Human User Interface
13.1 | Manufacturer
13.2 | Equipment number / Model
13.3 | Country of manufacture
13.4 | IP Rating | IP
13.5 | Supply Voltage | V ac/V dc
13.6 | Front Panel Dimensions | H x W x D
13.7 | Screen Size | mm
13.8 | Screen Resolution | Pixels
13.9 | Memory Capacity | MB
13.1 | PLC Communication Protocol
13.11 | Programming PC Communication Protocol
13.12 | Brightness | High/Normal
14 | Ethernet Switch/Fibre Optic Converter
14.1 | Manufacturer
14.2 | Equipment number / Model
14.3 | Country of manufacture
14.4 | Supply Voltage | V ac/V dc
14.5 | Copper Ethernet Ports | Number of
14.6 | Fibre Optic Ports | Number of
14.7 | Temperature Rating | °C
14.8 | Fibre Optic Data Rate | Mbits/sec
14.9 | Copper Ethernet Data Rate | Mbits/sec
14.1 | Conformal Coating | Yes/No
15 | Switchboard Light
15.1 | Manufacturer
15.2 | Equipment number / Model
15.3 | IP Rating | IP
15.4 | Power Rating | W
15.5 | Voltage | Vdc
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Electric Motor
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Electric Motor
Number |  | Units | Specification | Offered | Additional Comments
1 | Manufacturer Information
1.1 | Manufacturer
1.2 | Equipment type / Make
1.3 | Equipment number / Model
1.4 | Country of manufacture
2 | Motor Details
2.1 | Manufactured to Standard | AS/IEC/NEMA/ANSI
2.2 | Frame Size
2.3 | Mounting Arrangement
2.4 | No. Poles | Number of
2.5 | Number of Speeds (single/double)
2.6 | Speed - Full Load | RPM
2.7 | Output Power | kW
2.8 | Frequency | Hz
2.9 | Rated Voltage | V ac
2.1 | Current - Full Load | A/Ph
2.11 | Current - Locked Rotor | A/Ph
2.12 | Current - No Load | A/Ph
2.13 | Power Factor - Full Load (Cos φ)
2.14 | Power Factor - No Load (Cos φ)
2.15 | Method of Cooling (IEC 60034-6)
2.16 | Insulation Class
2.17 | Duty (IEC 60034-1)
2.18 | Enclosure IP Rating (to AS 60529) | IP
2.19 | Temperature Rise | ºC
2.2 | Ambient temperature (min / max) | ºC
2.21 | Duty Cycle/Load Cycle (Maximum)
2.22 | Starts Per Hour (Maximum) | Number of
2.23 | Noise Level: | dB (A) @ 1m
2.24 | Efficiency - Full Load: | %
2.25 | Efficiency - No Load: | %
3 | Protection Provided
3.1 | Motor Winding RTD's Per Phase | Number of
3.2 | Drive End Bearing RTD | Yes/No
3.3 | Non-Drive End Bearing RTD | Yes/No
3.4 | Motor Thermistors Per Phase | Number of
3.5 | Motor Heater Installed | Yes/No
3.6 | Motor Heater Rating | W
3.7 | Surface Treatment Category (ISO 12994-5) | Low/Med/High
4 | Motors Operating with Variable Speed Drives
4.1 | Suitable for VSD Operation | Yes/No
4.2 | Maximum Operating Speed | RPM
4.3 | Minimum Operating Speed | RPM
4.4 | Ventilation Fan Required Below | RPM
4.5 | Ventilation Fan Provided | Yes/No
4.6 | Insulated Bearings | Yes/No | State: DE, NDE or both
4.7 | Shaft Earth Brush Installed | Yes/No
4.8 | Terminal Box Earth for Motor Cables | Yes/No
4.9 | No. Cable Earth Terminals | Number of
4.1 | Terminal Box to Frame Bond Strap | Yes/No
5 | Bearings
5.1 | Type
5.2 | Bearing Life (L10h)
5.3 | Rotation | One/Both
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## LV Switchboard
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | LV Switchboard
Number |  | Units | Specification | Offered | Additional Comments
1 | Manufacturer Information
1.1 | Manufacturer
1.2 | Equipment type / Make
1.3 | Equipment number / Model
1.4 | Country of manufacture
2 | Design Information
2.1 | Design Life | Years | 25
2.2 | Derating Applied | %
2.3 | Location of Switchboard | Indoor/Outdoor
3 | Supply System Conditions
3.1 | Voltage | V ac | 400/230
3.2 | Frequency | Hz | 50 Hz ± 2%
3.3 | Voltage Unbalance | % | < 5
3.4 | LV Supply Star Point |  | Direct Earthed Neutral
3.5 | Single Phase Voltage | V ac | 230 (+10%, -6%)
3.6 | Control Voltage | V dc | 24
3.7 | Ambient Temperature Range | °C | -5/50
3.8 | Locational Environment |  |  |  | Indoor/outdoor/ coastal region/etc
4 | Electrical Requirements
4.1 | Type Test Certificate Required | Yes/No | Yes
4.2 | Type Test Certificate Number
4.3 | Coordination | Type
4.4 | Rated Current | A
4.5 | Short Circuit Current | kA for s
4.6 | Fault Protection
5 | Construction
5.1 | Form of Construction
5.2 | Degree of Protection to AS 60529 | IP
5.3 | Arc Containment to AS/NZS 61439
5.4 | Access |  | Front
5.5 | Cable Entry |  | Bottom
5.6 | Extendable Busbars | Yes/No
5.7 | Bus Tie
5.8 | Free Standing | Yes/No
5.9 | Stationary | Yes/No
5.1 | Material of Construction
5.11 | Protective Finish
5.12 | Colour | Opaline G32 / Rivergum G62 / Other
5.13 | Dimensions (H x W x D) | mm
5.14 | Material Thickness | mm
5.15 | Weight | kg
5.16 | Rain Hood | Yes/No
5.17 | Laptop shelf | Yes/No
5.18 | Sunshields | Yes/No
5.19 | Generator Connection Option | Yes/No
6 | Switchboard Plinth
6.1 | Material of Construction
6.2 | Material Thickness | mm
6.3 | Height | mm
6.4 | Type of Coating
SWITCHGEAR
7 | SAPN Main Switch/Load Limiting Device
7.1 | Circuit Breaker or Isolator |  | Circuit Breaker
7.2 | Manufacturer
7.3 | Equipment Number/Model
7.4 | Short Circuit Rating | kA for s
7.5 | Rated Voltage | V ac | 400
7.6 | Rated Continuous Current | A
7.7 | Unit Trip Setting | A
7.8 | Auxiliary Trip/Isolated Contacts | Yes/No
8 | Mains/Generator Changeover Switch
8.1 | Type | Automatic/Manual
8.2 | Manufacturer
8.3 | Equipment Number/Model
8.4 | Short Circuit Rating | kA for s
8.5 | Rated Voltage | V ac | 400
8.6 | Rated Continuous Current | A
8.7 | Auxiliary Contacts | Yes/No |  |  | Describe number and type
9 | Circuit Breakers
9.1 | Manufacturer
9.2 | 3 Phase + Neutral Circuits | Number of
9.3 | 1 Phase + Neutral Circuits | Number of
9.4 | 1 Phase RCD | Number of
9.5 | 3 Phase RCD | Number of
9.6 | Auxiliary Circuits - 240 V ac | Number of
9.7 | Auxiliary Circuits - 24 V dc | Number of
9.8 | Module Configuration |  | Fixed
9.9 | Remote Open/Close functionality
9.1 | ACB Modules | Number of
9.11 | Main Switch/Circuit Breakers Padlockable | Yes/No | Yes
9.12 | Trip Units |  | Inverse Time, Instantaneous
10 | Motor Circuit Breaker
10.1 | Manufacturer
10.2 | Equipment Number/Model
10.3 | Short Circuit Rating | kA for s
10.4 | Rated Voltage | V ac | 400
10.5 | Rated Continuous Current | A
10.6 | Unit Trip Setting | A
10.7 | Remote Open/Close functionality
10.8 | Auxiliary Contacts | Yes/No | Yes |  | Tripped, Isolated
11 | Motor Line Contactor
11.1 | Manufacturer
11.2 | Equipment Number/Model
11.3 | Short Circuit Rating | kA for s
11.4 | Rated Continuous Current | A
12 | Distribution Chassis
12.1 | Manufacturer
12.2 | Equipment Number/Model
12.3 | Number of Ways
12.4 | Short Circuit Rating | kA for s
12.5 | Rated Voltage | V ac | 400
12.6 | Rated Continuous Current | A
13 | Surge Arrester
13.1 | Manufacturer
13.2 | Equipment Number/Model
13.3 | Category (to AS/NZS 1768) | A/B/C1/C2/C3
13.4 | Discharge Current | kA
13.5 | Rated Voltage | V ac | 400
13.6 | Leakage Current | mA
13.7 | Supply Fuse/MCB type and size | A
13.8 | Auxiliary Feedback Contacts Provided | Yes/No | Yes
14 | Earth Leakage Protection
14.1 | Outgoing Circuits |  | N/A
14.2 | Submain Circuits |  | N/A
14.3 | Small Distribution Circuits |  | N/A
15 | Busbars
15.1 | Main Bar - Rated Current | A | 800
15.2 | Main Bar - Size | mm2
15.3 | Droppers - Rated Current | A
15.4 | Droppers - Size | mm2
16 | Auxiliaries
16.1 | Auxiliary Relays - Manufacturer
16.2 | Auxiliary Relays - Catalogue Number
16.3 | Auxiliary Relays - Contactor Rating | A
16.4 | Terminals - Manufacturer
16.5 | Terminals - Designation
16.6 | Cable Ferrules - Manufacturer
16.7 | Cable Ferrules - Designation
16.8 | Earth Leakage Relays - Manufacturer
16.9 | Earth Leakage Relays - Type/Model
16.1 | Phase Failure/Imbalance Relays - Manufacturer
16.11 | Phase Failure /Imbalance Relays - Type/Model
16.12 | Phase Failure /Imbalance Relays - Auxiliary Feedback Contacts Provided | Yes/No
16.13 | Current Transformers - Manufacturer
16.14 | Current Transformers - Type/Model
16.15 | Current Transformers - Accuracy Class
16.16 | Multi Function Meter - Manufacturer
16.17 | Multi Function Meter - Type/Model
16.18 | Multi Function Meter - Rated Voltage | Vac/Vdc | 400
16.19 | Multi Function Meter - Communications Type | Serial/Ethernet | Ethernet
Delivery / Lead Time
| Complete | Weeks |  |  | Maximum durations to be stated
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
LV Switchboard shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## HV Switchgear
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | HV Switchgear
Number |  | Units | Specification | Offered | Additional Comments
1 | General Information
1.1 | Manufacturer
1.2 | Equipment type / Make
1.3 | Equipment number / Model
1.4 | Country of manufacture
2 | Operating Data
2.1 | Design operating time | hr/day
2.2 | Minimum availability per 12 months | %
2.3 | Temperature derating applied | %
2.4 | Design life | Years
2.5 | Short time withstand current | kA / 3 sec
3 | Site Climatic Conditions
3.1 | Installation location | Indoor/Outdoor
3.2 | Ambient Air Temperature: Maximum | º C
3.3 | Ambient Air Temperature: Minimum | º C
3.4 | Ambient Air Temperature Yearly Average | º C
3.5 | Relative Humidity
3.6 | Pollution Degree
3.7 | Altitude | m
3.8 | Hazardous Area Classification
4 | Supply System Conditions
4.1 | Service Voltage, Phase
4.2 | Rated Voltage
4.3 | Frequency | Hz
4.4 | Earthing system
4.5 | BIL at altitude <=1000m | kV peak
5 | Construction
5.1 | Busbar system
5.2 | Dimension of a typical Incomer CB Cubicle (Height x Width x Depth | mm x mm x mm
5.3 | Cubicle Weight | kg
5.4 | Dimension of a typical Feeder CB Cubicle (Height x Width x Depth | mm x mm x mm
5.5 | Cubicle Weight | kg
5.6 | Dimension of Bus VT & Metering Cubicle (Height x Width x Depth | mm x mm x mm
5.7 | Cubicle Weight | kg
5.8 | Switchboard Weight | kg
5.9 | Degree of protection - Outer cover | IP
5.1 | Degree of protection - Inner partitions | IP
5.11 | Door type
5.12 | Interlocking Key type
5.13 | Arc containment
5.14 | Arc chutes and ducting
5.15 | Arc vent flaps with limit switches to detect gas release
5.16 | Arc fault protection (to IEC 62271-200)
5.17 | Internal arc withstand current | kA / sec
5.18 | Surge Arresters
5.19 | Operational Access
5.2 | Free standing
5.21 | Stationary
5.22 | Material of construction
5.23 | Material Thickness | mm
5.24 | Painting colour
5.25 | Painting treatment
5.26 | Extendable | Yes/No
5.27 | Manufactured to standard
6 | Cable Entry
6.1 | Incoming cable type
6.2 | Incoming cable size | mm2
6.3 | Feeder cable type
6.4 | Feeder cable size | mm2
6.5 | Incoming cable entry
6.6 | Feeder cable entry
6.7 | Cable insulation
6.8 | Power cable gland - material
6.9 | Power cable gland plate thickness | mm
6.1 | Control cable gland - material
6.11 | Control cable gland plate thickness | mm
7 | Busbars
7.1 | Rated current | A
7.2 | Busbar earth switch required
7.3 | Busbar Material
7.4 | Earth Bar
7.5 | Short time withstand current | kA / sec
7.6 | Peak withstand current | kA
7.7 | Power frequency withstand voltage | kV
7.8 | Impulse withstand voltage | kV
7.9 | Insulation type
SWITCHGEAR
8 | Circuit Breakers
8.1 | Manufacturer
8.2 | Equipment type / Make
8.3 | Equipment number / Model
8.4 | Incoming CB rating | A
8.5 | Feeder CB rating (motor) | A
8.6 | Bus Tie CB rating | A
8.7 | Feeder CB rating (transformer) | A
8.8 | Rated minimum voltage | kV
8.9 | Power Frequency Withstand voltage | kV
8.1 | Impulse withstand voltage | kV
8.11 | Rated short-circuit current | kA / sec
8.12 | Operating mechanism
8.13 | Rated short-circuit making current (1s) | kA
8.14 | Rated short-circuit breaking current (1s) | kA
8.15 | Withdrawable | Yes/No
8.16 | Spring charging motor voltage | V d.c.
8.17 | Anti-pumping Device | Yes/No
8.18 | CB truck pad-lockable in Test/Racked-out position | Yes/No
8.19 | Number of poles
8.2 | Number of phases
8.21 | Bus VT / Feeder VT | Fixed/Withdrawable
8.22 | Options
8.23 | Voltage Indicating Systems including lamps
8.24 | Circuit Breaker position | Aux switches
8.25 | Earthing Switch position | Aux switches
8.26 | Arc quenching device | Yes/No
8.27 | Remote operable | Yes/No
8.28 | Remote rackable | Yes/No
8.29 | Conditioning Monitoring | Yes/No
9 | Earthing Switch
9.1 | Manufacturer
9.2 | Equipment type / Make
9.3 | Equipment number / Model
9.4 | Bus earthing switch rated current | A
9.5 | Feeder earthing switch rated current | A
9.6 | Bus / Feeder earthing switch short-circuit making current | kA
9.7 | Earth Switch motorised control | Yes/No
9.8 | Arc quenching device | Yes/No
10 | Fused Isolators
10.1 | Manufacturer
10.2 | Equipment type / Make
10.3 | Equipment number / Model
10.4 | Rated current | A
10.5 | Rated minimum voltage | kV
10.6 | Power Frequency Withstand Voltage | kV
10.7 | Impulse withstand voltage | kV
10.8 | Rated short-circuit current (1s) | kA
10.9 | Indicators
10.1 | Auxillary Contacts (NO)
10.11 | Auxillary Contacts (NC)
10.12 | Number of phases
PROTECTION EQUIPMENT
11 | Protection Relay - Incomer
11.1 | Type
11.2 | Quantity
11.3 | Rating | VA
11.4 | Power supply | V
11.5 | Protection functions | ANSI Device Numbers
11.6 | Communication Protocol
12 | Protection Relay - ElectraNet
12.1 | Type
12.2 | Quantity
12.3 | Rating | VA
12.4 | Power supply | Vdc
12.5 | Protection functions | ANSI Device Numbers
12.6 | Communication Protocol
13 | Protection Relay - Feeder
13.1 | Type
13.2 | Quantity
13.3 | Rating | VA
13.4 | Power supply | Vdc
13.5 | Protection functions | ANSI Device Numbers
13.6 | Communication Protocol
POWER MONITORING EQUIPMENT
14 | Power Monitoring - Incomer
14.1 | Type
14.2 | Quantity
14.3 | Power supply | Vdc
14.4 | Functions
14.5 | Communication Protocol
15 | Power Monitoring - Feeder
15.1 | Type
15.2 | Quantity
15.3 | Power supply | Vdc
15.4 | Functions
15.5 | Communication Protocol
16 | Power Monitoring - Kiosk Substation Feeder
16.1 | Type
16.2 | Power supply | Vdc
16.3 | Functions
16.4 | Communication Protocol
AUXILIARIES
17 | Power Supply
17.1 | For spring loading
17.2 | Tripping Coil
17.3 | For protective relays, control and signalling
17.4 | Remote operation
17.5 | Remote racking
17.6 | Control bus voltage
17.7 | Protection bus voltage
17.8 | Auxilliary Supply Consumption - Continuous | W
17.9 | Auxilliary Supply Consumption - Peak | W
18 | Ethernet Switches for Communication
18.1 | Manufacturer
18.2 | Type
18.3 | Quantity
18.4 | Power supply | Vdc
18.5 | Hardware
18.6 | Ethernet Cables |  | Provided by?
19 | Current Transformer - Protection
19.1 | Manufacturer |  |  |  | Refer to TS0340
19.2 | Type
19.3 | Quantity
19.4 | Phase
19.5 | Class |  |  |  | Multiwind CTs may be used
19.6 | Capacity | VA
19.7 | Ratio | A / A
20 | Current Transformer - Earth Fault
20.1 | Manufacturer
20.2 | Type
20.3 | Quantity
20.4 | Phase
20.5 | Class
20.6 | Capacity | VA
20.7 | Ratio | A / A
21 | Current Transformer - Metering - SAW
21.1 | Manufacturer |  |  |  | Refer to TS0340
21.2 | Type
21.3 | Quantity
21.4 | Phase
21.5 | Class |  |  |  | Multiwind CTs may be used
21.6 | Capacity | VA
21.7 | Ratio | A / A
22 | Current Transformer - Metering - SAPN / ElectraNet
22.1 | Manufacturer
22.2 | Type
22.3 | Quantity
22.4 | Phase
22.5 | Class
22.6 | Capacity | VA
22.7 | Ratio | A / A
23 | Voltage Transformer - SAW
23.1 | Manufacturer
23.2 | Type
23.3 | Quantity
23.4 | Phase
23.5 | VA per phase
23.6 | Class
23.7 | Ratio | V / V
24 | Voltage Transformer - SAPN / ElectraNet
24.1 | Manufacturer
24.2 | Type
24.3 | Phase
24.4 | VA per phase
24.5 | Class
24.6 | Ratio | V / V
25 | Control Transformer
25.1 | Manufacturer
25.2 | Type
25.3 | Power rating | VA
25.4 | Primary / secondary voltage rating | V / V
26 | Voltmeter
26.1 | Range
26.2 | Selector switch
26.3 | Installation location
27 | Indicating Lamps
27.1 | Manufacturer
27.2 | Type
27.3 | Diameter | mm
27.4 | Voltage | V
28 | Test blocks - for relay maintenance test
28.1 | Manufacturer |  |  |  | Each protection relay shall be equipped with a test block which is installed on the front panel of the LV compartment
28.2 | Type |  |  |  | Refer to TS0340
29 | Control Fuses / MCBs and Aux Contacts
29.1 | Manufacturer |  |  |  | DC/AC MCBs shall be provided for different circuits. Certain MCBs require Aux contacts for monitoring MCB Open/Closed status
29.2 | Type
30 | Auxiliary Switches
30.1 | Manufacturer
30.2 | Type
31 | Push Buttons
31.1 | Manufacturer
31.2 | Type
31.3 | Diameter | mm
32 | Terminal blocks of LV Compartments
32.1 | Manufacturer
32.2 | Type
33 | Control Switch - Local closing/tripping |  |  |  | For panels with HV CBs, to be installed on the front panel of the LV compartment
33.1 | Manufacturer
33.2 | Type
34 | Control Switch - Local / Remote |  |  |  | To be installed on the front panel of the LV compartment
34.1 | Manufacturer
34.2 | Type
35 | Switchboard Internal Wiring
35.1 | Manufacturer
35.2 | Size and colour
36 | Other
36.1 | Anti-condensation heaters |  |  |  | The heaters shall be thermostatically controlled and individually RCD protected.
36.2 | Switchboard internal lighting |  |  |  | voltage
36.2
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Compliance
| Compliance with datasheet | Yes/No |  |  | (if no, please state non compliance in notes below)
Notes
Equipment shall comply with SA Water Technical Standard TS 0300 and TS 0340
Revision History
| Revision Description | Rev | Date | By | Chk

## Misc Elec Equipment
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Miscellaneous Electrical Equipment
Number |  | Units | Specification | Offered | Additional Comments
1 | Interior Building Lights
1.1 | Manufacturer
1.2 | Equipment number / Model
1.3 | IP Rating | IP
1.4 | Power Rating | W
1.5 | Emergency Supply | Yes/No
2 | Smoke Detector
2.1 | Manufacturer
2.2 | Equipment number / Model
3 | Outdoor Floodlights
3.1 | Manufacturer
3.2 | Equipment number / Model
3.3 | IP Rating | IP
3.4 | Power Rating | W
3.5 | Luminosity | lm
4 | Backup Battery
4.1 | Manufacturer
4.2 | Equipment number / Model
4.3 | Voltage | V dc
4.4 | Capacity | Ahr
5 | Battery Charger
5.1 | Manufacturer
5.2 | Equipment number / Model
5.3 | Output Voltage | V dc
5.4 | Charging Current | A
6 | ELV Power Supply
6.1 | Manufacturer
6.2 | Equipment number / Model
6.3 | Output Voltage | V ac/V dc
6.4 | Rated Current | A
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## VSD Datasheet
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Variable Speed Drive (VSD)
Number |  | Units | Specification | Offered | Additional Comments
1 | Manufacturer Information
1.1 | Manufacturer
1.2 | Equipment type / Make
1.3 | Equipment number / Model
1.4 | Country of manufacture
2 | Site Conditions
2.1 | Ambient temperature (min / max) | ºC | -5/50
2.2 | Humidity | % RH | 0/90
3 | Supply System Conditions
3.1 | Input Voltage Range, 3 Phase | V ac | 400 (+10%, -6%)
3.2 | Frequency | Hz | 50 ± 2%
3.3 | Voltage unbalance | % | < 5
3.4 | Single phase voltage range | V ac | 230 (+10%, -6%)
3.5 | Control voltage | V dc | 24
3.6 | Short circuit capacity (minimum) | kA for 1s | 15
4 | Motor Details
4.1 | Drive application
4.2 | Nominal Power Rating | kW
4.3 | Voltage | V ac | 400
4.4 | Frequency | Hz | 50
4.5 | Speed | rpm
4.6 | Full Load Current | A
4.7 | Cos φ
4.8 | IEC 60085 Thermal Class
4.9 | Motor Cable Length and Type | m
5 | VSD General
5.1 | Nameplate kW rating | kW |  |  | Derate as required
5.2 | Nameplate Current rating | A
5.3 | Design / Service life | Years | 15
5.4 | Rated ambient temperature | ºC | 45
5.5 | Derating applied | %
5.6 | Efficiency - VSD Only | %
5.7 | Efficiency - Total for all components | % |  |  | Total to be inclusive of VSD and all Filters (if required)
5.8 | Heat Load - VSD Only | kW
5.9 | Heat Load - Total for all components | kW |  |  | Total to be inclusive of VSD and all Filters (if required)
5.1 | Enclosure IP rating | IP
5.11 | Dynamic braking required | Yes/No
5.12 | Regenerative required | Yes/No
5.13 | Cooling Method
5.14 | Sound/Noise level @ 1m : Full Load | dB
5.15 | Conforming Standards | RCM conformity
5.16 | Mechanical shock protection
5.17 | Interference transmission
5.18 | Electrical noise suppression
5.19 | VSD Cubicle Paint Colour
5.2 | Acceleration Time : with specified load and 110% current limit
5.21 | Coast to Stop Time : with specified load and 110% current limit
5.22 | Interval between heatsink cooling fan replacement | Years | 10
5.23 | Conformal Coating level of pcb's | Yes | 3C3 to IEC 60721-3-3 (for WWTP) and 3C2 for Water PS
5.24 | RFI Compliance | Yes | C3 for 150m screened motor cable
5.25 | VSD Logic Control functionality |  | End of Curve Detection
5.26 | VSD Logic Control functionality |  | Multi Pump Controller
5.27 | VSD Logic Control functionality |  | Deragging Function
6 | VSD Input Details
6.1 | VSD upstream protection requirements
6.2 | VSD Input Isolator | Yes/No
6.3 | VSD Input Circuit Breaker | Yes/No
6.4 | Semiconductor Fuses Details
6.5 | Type
6.6 | Installation Location
6.7 | External Cubicle Included in Scope of VSD | Yes/No
6.8 | VSD Input Filter Details |  | State (if applicable)
6.9 | Input converter technology |  | State (if applicable)
6.1 | Number of pulses |  | State (if applicable)
6.11 | Input voltage range
6.12 | Input voltage tolerances |  | AS 60038
6.13 | Voltage sag
6.14 | Input voltage frequency range | Hz | 50 ± 2%
6.15 | Input power factor
6.16 | Total harmonic distortion at 100% load | %
6.17 | Max input current harmonic at 100% load:
7 | VSD Output Details
7.1 | Inverter technology
7.2 | Overload capacity |  | 110% for 60 sec
7.3 | Output frequency range | Hz
7.4 | Switching frequency | Hz
7.5 | Speed accuracy | % | ± 0.5%
7.6 | Fixed speeds | Number of
7.7 | Skip frequencies | Number of
8 | Sine Filter Details
8.1 | Sine Filter
8.2 | Sine Filter output dv/dt | V/μs
8.3 | Sine Filter output THD | %
8.4 | Sine Filter Efficiency | %
8.5 | Sine Filter Heat Load | kW
8.6 | Sine Filter - Installation Location
8.7 | Sine Filter - External Cubicle Included in Scope of VSD Supply | Yes/No
8.8 | Sine Filter - External Cubicle Dimensions | H x W x D
8.9 | Sine Filter - External Cubicle Paint Colour
9 | VSD Emergency Stop Input
9.1 | Emergency Stop Input
9.2 | Emergency Stop Input SIL Rating
9.3 | Safe Torque Off Functionality (STO) | Yes/No
9.4 | Emergency Stop Function Description | e.g. linear deceleration then lock rotor position
10 | VSD I/O and Communication
10.1 | Configurable I/O | Yes/No | Yes
10.2 | Analog inputs | mA | 4 - 20
10.3 | Analog outputs | mA | 4 - 20
10.4 | Digital inputs | V dc | 24 or volt-free relay
10.5 | Digital outputs | V dc | 24 or volt-free relay
10.6 | Digital outputs contact rating | A | State
10.7 | Programmable voltage free contacts | Yes/No | Yes
10.8 | Adjustable slip and start compensation | Yes/No
10.9 | Local display indication | Yes/No | Yes
10.1 | Intermittent over torque detection | Yes/No | Yes
10.11 | Number and type of winding thermal protection devices
10.12 | Number of bearing thermal protection devices
10.13 | Communication protocol |  | Ethernet IP
10.14 | Programming Port | Yes/No
10.15 | Number of communication ports
10.16 | Communication physical Interface
10.17 | Configuration Software | Model/Version
11 | VSD Details
11.1 | Supply cable size, number and type (minimum) | mm2
11.2 | Motor cable size, number and type (minimum) | mm2
11.3 | Motor cable length (maximum) | m
11.4 | Cable entry
11.5 | Mounting details
11.6 | VSD dimensions | H x W x D
11.7 | Clearance dimensions | H x W x D
11.8 | Total footprint (Total dimensions including clearances) | H x W x D
11.9 | Enclosure material
11.1 | Enclosure material thickness
11.11 | Gland plate (material type / thickness)
11.12 | Total Weight | kg
11.13 | Termination drawings provided | Yes/No
11.14 | Layout drawings provided | Yes/No
11.15 | Reliability (MTBF)
11.16 | PC Software included with Supply of VSD | Yes/No
Delivery / Lead Time
| Complete | Weeks |  |  | Maximum durations to be stated
| Spare parts minor components | Weeks |  |  | I/O cards, control board etc.
| Spare parts major components | Weeks |  |  | Power semiconductors etc.
Notes
VSD shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Diesel Generator
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Diesel Generator
Number |  | Units | Specification | Offered | Additional Comments
1 | General Information
1.1 | Manufacturer
1.2 | Equipment type / Make
1.3 | Equipment number / Model
1.4 | Country of manufacture
1.5 | Supplier
1.6 | Nominal Rating | KVA @ pf |  |  | The Contractor shalll confirm generator size prior to order
1.7 | Operation |  | Standby/intermittent or continuous operation
1.8 | Overall Length | mm
1.9 | Overall Width | mm
1.1 | Overall Height | mm
1.11 | Total Dry Mass | kg
1.12 | Total Wet Mass | kg
1.13
2 | Engine Details
2.1 | Type
2.2 | Manufacturer
2.3 | Model
2.4 | Country of Manufacture
2.5 | Power Rating (AS 2789) | kW
2.6 | Engine Speed | r/min
2.7 | No. of Cylinders
2.8 | Cylinder Bore | mm
2.9 | Cylinder Stroke | mm
2.1 | Piston Displacement | L
2.11 | Compression Ratio
2.12 | Engine Block Configuration
2.13 | Fuel Usage @ min. load | L/h
2.14 | Fuel Usage @ max. load | L/h
2.15 | Lube Oil Tank Capacity | L
2.16 | Max. Lube Oil Usage | L
3 | Alternator
3.1 | Make
3.2 | Type
3.3 | Rating | kVA
3.4 | Excitation
3.5 | Active Power @ p.f. = 0.8 | kW
3.6 | Rated Output @ p.f. = 1 | kW
3.7 | Voltage | V
3.8 | Frequency | Hz
3.9 | Speed | r/min.
3.1 | Permissible Overspeed | r/min.
3.11 | Efficiency @ FL and p.f. = 1 | %
3.12 | Efficiency @ FL and p.f. = 0.8 | %
3.13 | Enclosure Rating
3.14 | Insulation Class
3.15 | Output Voltage Regulation | %
3.16 | Total Harmonic Distortion | %
3.17
3.18 | Voltage Regulation
3.19 | Type
3.2 | Manufacturer
3.21 | Model
3.22 | Control Accuracy Rating
4 | Cooling System
4.1 | Type
4.2 | Radiator Type
4.3 | Radiator Cooling Capacity | kW
4.4 | Radiator Width | mm
4.5 | Radiator Height | mm
4.6 | Radiator Fan Capacity | m3/hr
4.7
4.8 | Fan Type
4.9 | Wire Guard Enclosure
4.1 | Radiator Ducting Provided | Y/N
4.11 | Required Fan Pressure | Pa
5 | Acoustic Enclosure
5.1 | Manufacturer's Name
5.2 | Country of Manufacture
5.3 | Dimensions (LxWxD) | mm
5.4 | Material of manufacture
5.5 | IP rating (to AS1939)
5.6 | Mass of largest removable panel | kg
5.7 | Sound Pressure Level at 1m | dB(A)
5.8 | Vibration Level | mm/sec
6 | Injectors and Governing System
6.1 | Injectors
6.2 | Type
6.3 | Manufacturer
6.4 | Model
6.5 | Service Interval | h
6.6
6.7 | Governing System
6.8 | Type
6.9 | Manufacturer
6.1 | Model
6.11 | Control Accuracy Rating (to AS 1789.4)
7 | Diesel Fuel System
7.1 | Diesel Fuel Tank Capacity | L
7.2 | Running Hours at full load | h
7.3 | Run Hours at reduced load | h
7.4 | Bunded | Y/N
8 | Exhaust System
8.1 | Engine Exhaust
8.2 | Exhaust Outlet
8.3 | Exhaust gas flowrate | Sm3/hr
8.4 | Admissible pressure drop
8.5
8.6 | Exhaust Silencer / Spark Arrester
8.7 | Type
8.8 | Manufacturer
8.9 | Size | mm
8.1 | Mass | kg
8.11
8.12 | Exhaust Stack
8.13 | Size | mm
8.14 | Raincap Provided | Y/N
8.15 | Support System Provided | Y/N
8.16
9 | Air Intake Filters
9.1 | Type
9.2 | Manufacturer
9.3 | Model
9.4 | Country of Manufacture
9.5 | No. Required
9.6 | Element Details
9.7 | Differential Press. Indicator
10 | Lube Oil System
10.1 | Pump
10.2 | Type
10.3 | Manufacturer
10.4 | Model
10.5
10.6 | Filter
10.7 | Type
10.8 | Element Type
10.9 | Manufacturer
10.1 | Model
10.11
10.12 | Tank
10.13 | Lube Oil Tank Capacity | L
10.14 | Max. Lube Oil Usage | L
11 | Alternator
11.1 | Starter Motor
11.2 | Type
11.3 | Manufacturer
11.4 | Model
11.5 | Voltage & Type
11.6
11.7 | Starting Batteries
11.8 | Type
11.9 | Manufacturer
11.1 | Model
11.11 | Number
11.12 | Load Rating | Ah
11.13 | Nominal Voltage | V
11.14 | Design Life Expectancy | Years
11.15 | Mounting Location
11.16
11.17 | Battery Charger
11.18 | Manufacturer
11.19 | Model
11.2 | Dimensions (L x W x D) | mm
11.21 | Supply Voltage | V
11.22 | Rated Output Voltage | V
11.23 | Rated Full Load Current | A
12 | Noise and Vibration
12.1 | Noise
12.2 | SPL @ 63 Hz (at full load) | dB(A)
12.3 | SPL @ 125 Hz (at full load) | dB(A)
12.4 | SPL @ 250 Hz (at full load) | dB(A)
12.5 | SPL @ 500 Hz (at full load) | dB(A)
12.6 | SPL @ 1000 Hz (at full load) | dB(A)
12.7 | SPL @ 2000 Hz (at full load) | dB(A)
12.8 | SPL @ 4000 Hz (at full load) | dB(A)
12.9 | SPL @ 8000 Hz (at full load) | dB(A)
12.1 | Overall dB(A) @ 1 m ref. 20 x 10-6 Pa: | dB(A)
12.11
12.12 | Vibration
12.13 | Level @ Full Load | mm/s
13 | Load Bank
13.1 | Manufacturer
13.2 | Country of Manufacture:
13.3 | Dimensions (LxWxD)
13.4 | Full load rating | kW
13.5 | Number of loading stages
13.6 | Material of Manufacture
13.7 | Element Material
13.8 | Temp of Discharge Air | °C
14 | Main Circuit Breaker
14.1 | Manufacturer
14.2 | Model
14.3 | Current Rating | A
14.4 | Fault Rating | kA
15 | Alternator
15.1 | Manufacturer
15.2 | Model
15.3 | Dimensions (L x W x D) | mm
15.4 | Enclosure IP rating | IP
15.5 | Enclosure material
15.6 | Volt-free contacts available | number of
15.7 | Analog outputs available | number of
Certified Testing
| Engine | Required/Not Required
| Generator | Required/Not Required
| Noise | Required/Not Required
| Vibration | Required/Not Required
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Telemetry
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Telemetry
Number |  | Units | Specification | Offered | Additional Comments
1 | General Information - Telemetry Unit
1.1 | Manufacturer
1.2 | Equipment type / Make
1.3 | Equipment number / Model
1.4 | Country of manufacture
1.5 | Supplier
1.6 | Supply Voltage | V
1.7 | Power consumption | W
1.8 | Overall Length | mm
1.9 | Overall Width | mm
1.1 | Overall Height | mm
2 | End #1
2.1 | Location
2.2 | Number of Analog Inputs
2.3 | Number of Analog Outputs
2.4 | Number of Digital Inputs
2.5 | Number of Digital Outputs
2.6 | Rated Voltage Digital Inputs | V ac/V dc
2.7 | Rated Current Digital Inupts | A
2.8 | Rated Voltage Digital Outputs | V ac/V dc
2.9 | Rated Current Digital Outputs | A
3 | End #2
3.1 | Location
3.2 | Number of Analog Inputs
3.3 | Number of Analog Outputs
3.4 | Number of Digital Inputs
3.5 | Number of Digital Outputs
3.6 | Rated Voltage Digital Inputs | V ac/V dc
3.7 | Rated Current Digital Inupts | A
3.8 | Rated Voltage Digital Outputs | V ac/V dc
3.9 | Rated Current Digital Outputs | A
4 | Radio Equipment
4.1 | Manufacturer
4.2 | Model
4.3 | Supply Voltage | V
4.4 | Power Consumption | W
4.5 | Radio Frequency Band | MHz
4.6 | Transmission Power | W
5 | Backup Battery
5.1 | Manufacturer
5.2 | Model
5.3 | Supply Voltage | V
5.4 | Capacity | Ah
5.5 | Operational Time | h
5.6 | Dimensions (L x W x D) | mm
6 | Antenna
6.1 | Manufacturer
6.2 | Model
6.3 | Type (Yagi, Whip, Low Profile)
6.4 | Number of Elements (if Yagi) | No
6.5 | Mounting Height (above ground) | m
6.6 | Antenna cable | low/high loss
6.7 | Antenna Mast Earthing | Y/N
6.8 | Lightning and Surge Protection | Y/N
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300, TS0360, TS0302
Revision History
| Revision Description | Rev | Date | By | Chk

## Local Telemetry Bridge
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Local Telemetry Bridge
Number |  | Units | Specification | Offered | Additional Comments
1 | General Information
1.1 | Manufacturer
1.2 | Equipment type / Make
1.3 | Equipment number / Model
1.4 | Country of manufacture
1.5 | Supplier
1.6 | Supply Voltage | V
1.7 | Power consumption | W
1.8 | Radio Frequency Band | MHz
1.9 | Transmission Power | W
1.1 | Maximum Link Distance | m
1.11 | Ethernet Ports | No
1.12 | IP Rating | IP
1.13 | Temperature rating | °C
1.14 | Overall Length | mm
1.15 | Overall Width | mm
1.16 | Overall Height | mm
2 | Backup Battery
2.1 | Manufacturer
2.2 | Model
2.3 | Supply Voltage
2.4 | Capacity
2.5 | Operational Time
2.6 | Dimensions (L x W x D) | mm
3 | Antenna
3.1 | Manufacturer
3.2 | Model
3.3 | Type (Yagi, Whip, Low Profile)
3.4 | Number of Elements (if Yagi) | No
3.5 | Mounting Height (above ground) | m
3.6 | Antenna cable | low/high loss
3.7 | Antenna Mast Earthing | Y/N
3.8 | Lightning and Surge Protection | Y/N
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300, TS0360, TS0302
Revision History
| Revision Description | Rev | Date | By | Chk

## Turbidity Analyser
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Turbidity Analyser |  | Tag No.
Number |  | Units | Specification | Offered | Additional Comments
1 | Fluid Details
1.1 | Process fluid
1.2 | Solid Content | % by Wt.
1.3 | Solid Size | mm
1.4 | Fluid Temperature | °C
1.5 | Density | kg/m3
1.6 | Viscosity | cP
1.7 | pH Value
1.8 | TDS | mg/L
1.9 | Max. Pressure | m
2 | Installation Conditions
2.1 | Location
2.2 | Ambient Temperature | °C
2.3 | Installation Type
3 | Materials
3.1 | Probe
3.2 | O-Ring
3.3 | Bayonet
3.4 | Converter/Transmitter
3.5 | Cable Sheath
3.6 | Probe Flange
4 | Sensor
4.1 | Type
4.2 | Manufacturer
4.3 | Model No.
4.4 | Measuring Range | NTU
4.5 | Accuracy | % of span
4.6 | Repeatability | % of span
4.7 | Response Time | min
4.8 | IP Rating | IP
4.9 | Process Connection
4.1 | Automatic Cleaning | Y/N
5 | Transmitter
5.1 | Manufacturer
5.2 | Model No.
5.3 | Mounting Style
5.4 | IP Rating | IP
5.5 | Communications Protocol
5.6 | Output signal
5.7 | Digital display | Y/N
5.8 | Pressure (max) | bar
5.9 | Temperature Range | °C
5.1 | Connector type
5.11 | Supply Voltage | V
5.12 | Frequency | Hz
5.13 | Power consumption | W
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Conductivity Analyser
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Conductivity Analyser |  | Tag No.
Number |  | Units | Specification | Offered | Additional Comments
1 | Fluid Details
1.1 | Process fluid
1.2 | Solid Content | % by Wt.
1.3 | Solid Size | mm
1.4 | Fluid Temperature | °C
1.5 | Density | kg/m3
1.6 | Viscosity | cP
1.7 | Chlorides | mg/L
1.8 | Ammonia | mg/L
1.9 | pH Value
1.1 | TDS | mg/L
1.11 | Max. Pressure | m
2 | Installation Conditions
2.1 | Sample Flow | m3/s
2.2 | Sample Pressure | bar
2.3 | Sample connection | "NPT
3 | Materials
3.1 | Sensor
3.2 | Flow hardware
3.3 | Transmitter
3.4 | Connection type
4 | Sensor
4.1 | Type
4.2 | Manufacturer
4.3 | Model No.
4.4 | Measuring Range | µS/cm
4.5 | Accuracy | % of span
4.6 | Repeatability | % of span
4.7 | Response Time | min
4.8 | IP Rating | IP
4.9 | Process Connection
4.1 | Operating Temperature range | °C
4.11 | Calibration certificate | Req/not Req?
5 | Transmitter
5.1 | Manufacturer
5.2 | Model No.
5.3 | Mounting Style
5.4 | IP Rating | IP
5.5 | Communications Protocols
5.6 | Output signal
5.7 | Digital outputs
5.8 | Mounting Style
5.9 | Digital display | Y/N
5.1 | Resolution | µS/cm
5.11 | Supply Voltage | V
5.12 | Frequency | Hz
5.13 | Power consumption | W
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## pH Analyser
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | pH Analyser |  | Tag No.
Number |  | Units | Specification | Offered | Additional Comments
1 | Installation and Service Conditions
1.1 | Process fluid
1.2 | Fluid temperature (min / max) | °C
1.3 | Fluid density | kg/m³
1.4 | Fluid viscosity | cP
1.5 | Solid Size (min / max) | %
1.6 | Minimum fluid conductivity | µS/cm
1.7 | Solids in feed | t/hr
1.8 | S.G. (Water = 1000kg/m³)
1.9 | Magnetic material content | %
1.1 | Magnetic susceptible material | %
1.11 | Hazardous area classification
1.12 | Hazardous area certification
1.13 | Environmental conditions
1.14 | Ambient temperature (min / max) | °C
1.15 | Humidity | % RH
2 | Sensor
2.1 | Manufacturer
2.2 | Model no.
2.3 | Part no.
2.4 | Available range | pH
2.5 | Measuring principle
2.6 | Measuring task
2.7 | Process connection - Size | inch
2.8 | Process connection - Type
2.9 | Process connection - Material
2.1 | Housing - IP rating | IP
2.11 | Housing - Material
2.12 | Housing - Mounting
2.13 | Body material
2.14 | Wetted body material
2.15 | Mounting position
2.16 | Insertion length
2.17 | Calibration requirements
2.18 | Maintenance requirements
2.19 | Calibration certificate | Req/Not Req
3 | Transmitter
3.1 | Manufacturer
3.2 | Accuracy | %
3.3 | Linearity | %
3.4 | Repeatability | %
3.5 | Power supply | V
3.6 | Power consumption | W
3.7 | Signal output | mA
3.8 | Alarm Signal | Yes / No
3.9 | Operating temperature range | °C
3.1 | Electrical connection
3.11 | Available range | pH
3.12 | Calibrated range | pH
3.13 | Range setpoint | pH
3.14 | Direct / remote electronics
3.15 | Control mode
3.16 | Response time
3.17 | Local indication
3.18 | Calibration requirements
3.19 | Maintenance requirements
3.2 | Calibration certificate
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Flow Switch
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Flow Switch |  | Tag No.
Number |  | Units | Specification | Offered | Additional Comments
1 | Process Details
1.1 | Process fluid/solid type
1.2 | Solid Content | % by Wt.
1.3 | Solid Size | mm
1.4 | Material Temperature | °C
1.5 | Density | kg/m3
1.6 | Viscosity | cP
1.7 | pH Value
1.8 | TDS | mg/L
1.9 | Max. Pressure | m
1.1 | Minimum flow | L/s
1.11 | Maximum flow | L/s
2 | Installation Conditions
2.1 | Location
2.2 | Ambient Temperature | °C
2.3 | Installation Type
3 | Materials
3.1 | Sensor
3.2 | External enclosure
3.3 | Transducer support
3.4 | Fasteners
4 | Sensor
4.1 | Type
4.2 | Manufacturer
4.3 | Model No.
4.4 | Measurement method
4.5 | Measurement Range | cm/s
4.6 | IP Rating - Internal
4.7 | IP Rating - External
4.8 | Mounting Style
4.9 | Mounting Size
4.1 | Ambient Temp. Rating | °C
4.11 | Self Cleaning | Y/N
5 | Electrical
5.1 | Supply Voltage | V
5.2 | Frequency | Hz
5.3 | Maximum cable length | m
5.4 | Signal Type
5.5 | Configuration (NO/NC)
5.6 | No. Outputs
5.7 | Hazardous Area Ratings | Req/Not req
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Level Switch
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Level Switch |  | Tag No.
Number |  | Units | Specification | Offered | Additional Comments
1 | Process Details
1.1 | Process fluid/solid type
1.2 | Solid Content | % by Wt.
1.3 | Solid Size | mm
1.4 | Material Temperature | °C
1.5 | Density | kg/m3
1.6 | Viscosity | cP
1.7 | pH Value
1.8 | TDS | mg/L
1.9 | Max. Pressure | m
1.1 | Minimum flow | L/s
1.11 | Maximum flow | L/s
2 | Installation Conditions
2.1 | Location
2.2 | Ambient Temperature | °C
2.3 | Installation Type | Top, side ,
2.4 | Vessel material |  |  |  | Plastic, Concrete, Steel, Fibreglass
2.5 | Distance from mount to switch point | mm
3 | Materials
3.1 | Sensor
3.2 | External enclosure
3.3 | Transducer support
3.4 | Fasteners
4 | Sensor
4.1 | Type
4.2 | Manufacturer
4.3 | Model No.
4.4 | Measurement method |  |  |  | (Capacitance, Vibration, Conductivity, pressure, Radar)
4.5 | Measurement Range | cm/s
4.6 | IP Rating - Internal
4.7 | IP Rating - External
4.8 | Mounting Style
4.9 | Mounting Size
4.1 | Ambient Temp. Rating | °C
4.11 | Self Cleaning | Y/N
5 | Electrical
5.1 | Supply Voltage | V
5.2 | Frequency | Hz
5.3 | Maximum cable length | m
5.4 | Signal Type
5.5 | Configuration (NO/NC)
5.6 | No. Outputs
5.7 | Hazardous Area Ratings | Req/Not req
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Flowmeter
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Flowmeter |  | Tag No.
Number |  | Units | Specification | Offered | Additional Comments
1 | General
1.1 | Service Description
1.2 | P&ID Number
1.3 | Equipment / Line Number
1.4 | Nominal Diameter | DN (mm)
1.5 | Pipe Material
1.6 | Quantity
1.7 | Technical Specification |  | TS 0260
1.8 | Design Life | years | 25
1.9
2 | Operating Conditions
2.1 | General
2.2 | Installation Orientation |  |  |  | i.e. Vertical/Horizontal Refer to TS 0260 for conditions of installation within SA Water Assets Facilities
2.3 | Environment
2.4 | Location | Indoor/Outdoor/In-pit/Buried
2.5 | Atmospheric Corrosivity Category | AS2312
2.6 | Ambient Temperature | °C | -5 (min) / 50 (max)
2.7 | Humidity | % RH | 0 / 90
2.8 | Hazardous Area Classification |  |  |  | i.e. Zone, Gas Group/Dust Group, Temperature Class
2.9 | Process fluid properties
2.1 | Fluid Type Description |  | ` |  | Potable, non-potable, raw water, wastewater, etc
2.11 | Total Dissolved Solids (by EC) | mg/L
2.12 | Solids Content | % by Wt.
2.13 | Solids Size | mm
2.14 | Conductivity | µS/cm (min - max)
2.15 | Turbidity | NTU
2.16 | Temperature | °C (min / max)
2.17 | Density | kg/m³
2.18 | Viscosity | cP
2.19 | Chlorides | mg/L
2.2 | pH
2.21 | Total Hardness as CaCO3 | mg/L as CaCO3
2.22 | Chlorine - Total | mg/L
2.23 | Monochloramine | mg/L
2.24 | Chlorine - Free | mg/L
2.25 | Hydraulic conditions
2.26 | Flow Direction | uni / bi directional
2.27 | Flow Rate (min) | L/s
2.28 | Flow Rate (max) | L/s
2.29 | Flow Rate (ave) / (nominal) | L/s
2.3 | Flow Velocity (min / norm / max) | m/s
2.31 | Maximum Operating Pressure (excluding surge) | kPa g
2.32 | Maximum Operating Pressure (including surge) | kPa g
2.33 | Minimum Operating Pressure (including surge) | kPa g |  |  | Vendors shall confirm the nominated flowmeter can operate without fault with pressure variations whereby vacuum pressure can form for a short period of time.
2.34 | Static Pressure (no flow) | kPa g
2.35 | Design Pressure | kPa g
2.36 | Field Hydrostatic test pressure | kPa g
3 | Flowmeter Details
3.1 | General
3.2 | Manufacturer |  | Vendor to Advise
3.3 | Model Number |  | Vendor to Advise
3.4 | Country of Origin |  | Vendor to Advise
3.5 | Manufacturing Standard |  | Vendor to Advise
3.6 | IP Rating |  | Vendor to Advise
3.7 | Available Range | TBC by Designer | Vendor to Advise
3.8 | Measuring Principle |  | Vendor to Advise |  | i.e. Magnetic/Thermal Mass/Ultrasonic/DP/Coriolis etc.
3.9 | Measuring Task |  | Continuous Flow
3.1 | Pressure Rating | PN (bar) | Vendor to Advise
3.11 | Allowable Operating Pressure (excluding surge) | kPa g | Vendor to Advise
3.12 | Maximum Allowable Operating Pressure (including surge) | kPa g | Vendor to Advise
3.13 | Allowable Site Test Pressure | kPa g | Vendor to Advise
3.14 | Headloss across flowmeter at maximum flow | kPa g | Vendor to Advise
3.15 | Minimum straight length of pipeline required upstream of valves/pipe direction changes | mm |  |  | i.e. Provide Any Existing Restriction Details Here
3.16 | Minimum straight length of pipeline required downstream of valves/pipe direction changes | mm |  |  | i.e. Provide Any Existing Restriction Details Here
3.17 | Flanged end connections
3.18 | Flange Face Type | O-ring / raised face / flat face
3.19 | Bolt Hole Drilling Pattern | AS4087
3.2 | Flange Sealing Area Surface Finish | Coated / Gramophone
3.21 | Flange Load Limits | N (axial) / N (radial) | Vendor to Advise
3.22 | Transmitter
3.23 | Accuracy | % | ± 0.1
3.24 | Linearity | % | Vendor to Advise
3.25 | Repeatability | % | Vendor to Advise
3.26 | Power Supply | VAC | 230
3.27 | Power Consumption | W | Vendor to Advise
3.28 | Operating Temperature Range | °C | Vendor to Advise
3.29 | Available Range | L/s | Vendor to Advise
3.3 | Calibrated Range | L/s | Vendor to Advise
3.31 | Range Setpoint | L/s | Vendor to Advise
3.32 | Response Time |  | Vendor to Advise
3.33 | Transmitter Mounting | Integral / Remote | Remote
3.34 | Local Indication |  | Yes |  | i.e. LCD Display
3.35 | IP Rating |  | Vendor to Advise
3.36 | Signal Output | mA | 4-20 |  | i.e. With Pulse Output for Totaliser
3.37 | Totalizer | Yes / No | Yes
3.38 | Alarm Signal | Yes / No | Vendor to Advise |  | i.e. Via Comms
3.39 | Empty Pipe Detection | Yes / No | No |  | i.e. Via Comms
3.4 | Communications Interfaces Available |  | Vendor to Advise |  | i.e. Modbus, Ethernet IP
3.41 | Electrical Connections (Type, Quantity) |  | Vendor to Advise |  | i.e. M20
3.42 | Cable Type Between Meter and Transmitter |  | Vendor to Advise |  | i.e. For Specific Vendor Supplied Cabling
3.43 | Cable Length Between Meter and Transmitter | m | Vendor to Advise |  | i.e. For Specific Vendor Supplied Cabling
3.44 | Cable Type / Length Limitations / Requirements Between Transmitter and Control Systems |  | Vendor to Advise |  | i.e. For Ethernet Systems
3.45 | Materials of Construction
3.46 | Body |  | Vendor to Advise
3.47 | Liner |  | Vendor to Advise
3.48 | Tube/Meter Casing |  | Vendor to Advise
3.49 | Flanges |  | Vendor to Advise
3.5 | Electrode
3.51 | Electronics Housing |  | Vendor to Advise
3.52 | Testing, Certification and Documentation
3.53 | Flowmeter Product Certification | Yes | Vendor to Advise
3.54 | Hazardous Area Ceritification | Yes / No | No |  | i.e. IECEx, ANZEx
3.55 | Hazardous Area Protection Technique Data | Yes / No | No |  | i.e. Ex d, Ex ia etc.
3.56 | Coating Product Certification |  | AS/NZS 4158 (for FBE) or APAS 2975P/2977P (for high build 2 pack epoxy)
3.57 | Calibration Certification / Requirements | Yes / No | Yes |  | i.e. Vendor to Advise Specifics
3.58 | Coating Repair Procedure | Yes / No | Yes
3.59 | Dimensioned Enginering Drawing | Yes / No | Yes
3.6 | Manufacturing Inspection and Test Plan (ITP) | Yes / No | Yes
3.61 | Installation, Operation and Maintenance Manual | Yes / No | Yes
3.62 | Dimensions and weight
3.63 | Flange Face to Face | mm | Vendor to Advise
3.64 | Flange Sealing Face Internal Diameter | mm | Vendor to Advise
3.65 | Total Weight | kg | Vendor to Advise
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0260
Revision History
| Revision Description | Rev | Date | By | Chk
Note - insert drawings, photos, etc. to inform vendor of installation details.
Refer to latest version of this Datasheet (SAWD-ENG-0200) on the SA Water website

## Pressure Transmitter
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Pressure Transmitter |  | Tag No.
Number |  | Units | Specification | Offered | Additional Comments
1 | Process Details
1.1 | Process fluid/gas type
1.2 | Solid Content | % by Wt.
1.3 | Solid Size | mm
1.4 | Fluid/gas Temperature | °C
1.5 | Density | kg/m3
1.6 | Viscosity | cP
1.7 | pH Value
1.8 | TDS | mg/L
1.9 | Minimum pressure | kPa
1.1 | Maximum pressure | kPa
2 | Installation Conditions
2.1 | Location
2.2 | Ambient Temperature | °C
2.3 | Isolation valve required? (Type/size/material)
2.4 | Installation Type
3 | Materials
3.1 | Body
3.2 | Diaphram
3.3 | Process Connection | " NPT
3.4 | Pressure Fittings
3.5 | Pipe to Transmitter
4 | Sensor
4.1 | Type
4.2 | Manufacturer
4.3 | Country of origin
4.4 | Model No.
4.5 | Measurement method
4.6 | Calibration Range | kPa
4.7 | IP Rating
4.8 | Maximum rated pressure | kPa
4.9 | Accuracy | %
4.1 | Repeatability | %
4.11 | Ambient Temp. Rating | °C
4.12 | Integrated digital display | Y/N
4.13 | Display Range | kPa
4.14 | No. of digits
4.15 | Calibration certificate | Req/Not req
5 | Electrical
5.1 | Supply Voltage | V
5.2 | Frequency | Hz/dc
5.3 | Maximum cable length | m
5.4 | Output Signal Type |  |  |  | Analog
5.5 | Communications
5.6 | No. Digital Outputs | No. and Type
5.7 | Configuration (NO/NC)
5.8 | Load impedance | Ohms
5.9 | Hazardous Area Ratings | Req/Not req |  |  | list
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Hydrostatic Level Transmitter
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Hydrostatic Level Transmitter |  | Tag No.
Number |  | Units | Specification | Offered | Additional Comments
1 | Process Details
1.1 | Process fluid
1.2 | Solid Content | % by Wt.
1.3 | Solid Size | mm
1.4 | Fluid Temperature | °C
1.5 | Density | kg/m3
1.6 | Viscosity | cP
1.7 | pH Value
1.8 | TDS | mg/L
1.9 | Minimum pressure | kPa
1.1 | Maximum pressure | kPa
2 | Installation Conditions
2.1 | Location
2.2 | Ambient Temperature | °C
2.3 | Mounting system |  |  |  | installed in stilling tube, suspended by cable
2.4 | Installation Type
3 | Materials
3.1 | Body
3.2 | Diaphram
3.3 | Process Connection | " NPT
3.4 | Pressure Fittings
3.5 | Pipe to Transmitter
4 | Sensor
4.1 | Type
4.2 | Manufacturer
4.3 | Country of origin
4.4 | Model No.
4.5 | Measurement method
4.6 | Calibration Range | kPa
4.7 | IP Rating
4.8 | Maximum rated pressure | kPa
4.9 | Accuracy | %
4.1 | Repeatability | %
4.11 | Ambient Temp. Rating | °C
4.12 | Integrated digital display | Y/N
4.13 | Display Range | kPa
4.14 | No. of digits
4.15 | Calibration certificate | Req/Not req
4.16 | Sensor Cable length | m
5 | Electrical
5.1 | Supply Voltage | V
5.2 | Frequency | Hz/dc
5.3 | Maximum cable length | m
5.4 | Output Signal Type |  |  |  | Analog
5.5 | No. Digital Outputs | No. and Type
5.6 | Configuration (NO/NC)
5.7 | Load impedance | Ohms
5.8 | Hazardous Area Ratings | Req/Not req |  |  | list
5.9 | Communications
5.1 | Remote Display / Breather J Box
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Radar Level Transmitter
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Radar Level Transmitter |  | Tag No.
Number |  | Units | Specification | Offered | Additional Comments
1 | Process Details
1.1 | Process - Fluid/Solid
1.2 | Solid Content | % by Wt.
1.3 | Solid Size | mm
1.4 | Process Temperature | °C
1.5 | Density | kg/m3
1.6 | Viscosity | cP
1.7 | pH Value
1.8 | TDS | mg/L
1.9 | Dielectric
1.1 | Maximum pressure | kPa
1.11 | Maximum Range | mm
2 | Installation Conditions
2.1 | Location
2.2 | Ambient Temperature | °C
2.3 | Agitated vessel | Y/N
2.4 | Process isolation valve required? | Y/N |  |  | (Type/size/material)
2.5 | Installation Type
3 | Materials
3.1 | Body
3.2 | Wetted parts
3.3 | Process Connection | " NPT
3.4 | Pressure Fittings
3.5 | Stand Pipe diameter/height
4 | Sensor
4.1 | Type | GHz
4.2 | Manufacturer
4.3 | Country of origin
4.4 | Model No.
4.5 | Minimum Span | mm
4.6 | Maximum Span | mm
4.7 | IP Rating | IP
4.8 | Maximum rated pressure | kPa
4.9 | Accuracy | mm
4.1 | Repeatability | mm
4.11 | Ambient Temp. Rating | °C
4.12 | Integrated digital display | Y/N
4.13 | Display Range | m
4.14 | No. of digits
4.15 | Beam angle (total) | °
4.16 | Mounting Bracket required | Y/N
5 | Electrical
5.1 | Supply Voltage | V
5.2 | Frequency | Hz/dc
5.3 | Maximum cable length | m
5.4 | Output Signal Type |  |  |  | Analog (include transmitter fail modes)
5.5 | Loop Powered | Y/N
5.6 | Configuration (NO/NC)
5.7 | Load impedance | Ohms
5.8 | Hazardous Area Ratings | Req/Not req |  |  | list
5.9 | Communications | HART/Bluetooth
5.1 | Remote Display | Y/N
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## UV Disinfection System
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | UV Disinfection System |  | P&ID No.
Number |  | Units | Specification | Offered | Additional Comments
1 | Installation and Service Conditions
1.1 | Type | - | Inline UV Reactor
1.2 | Quantity Required | unit | 3
1.3 | Configuration | - | Lead / Lag / Standby (Proposed) |  | Supplier to demonstrate that the proposed UV configuration provides the optimum energy efficiency.
1.4 | Equipment Function | - | Disinfection to reduce the risk of cryptosporidium breakthrough in treated water
1.5 | Equipment Tag Number | - | ME7001 / ME7002 / ME7003
1.6 | Maintenance Classification | - | Statutory
1.7 | Unit Design life | years | 25
1.8 | Operational Availability for Lead and Lag UV units | hrs/d | 24 hrs and 7 days a week |  | The UV unit shall also have option for operating intermittently
1.9 | Scheduled Downtime | hrs/yr | Supplier to advise |  | Non productive downtime which includes planned shutdowns and maintenance
1.1 | Environment | -
1.11 | Location | -
1.12 | Barometric Pressure | kPa
1.13 | Atmospheric Corrosivity Category (AS/NZS 2312) | -
1.14 | Climate Classification | -
1.15 | Outdoors Ambient Temperature Range | °C
1.16 | Outdoors Ambient Relative Humidity | %
1.17 | Indoors Ambient Temperature Range | °C
1.18 | Indoors Ambient Relative Humidity | %
2 | Vendor Information
2.1 | Supplier
2.2 | Manufacturer
2.3 | Place of Manufacture
2.4 | Model No.
3 | Required Electrical Supply
3.1 | Voltage | V AC
3.2 | Phase | -
3.3 | Frequency (nominal) | Hz
3.4 | Total harmonic distortion | %
3.5 | Allowable Sag/Swell Tolerance | %
3.6 | Allowable Sag/Swell Duration | s
3.7 | Allowable Power Interruption Tolerance | ms
4 | System Water Quality Data
4.1 | Process fluid | -
4.2 | Water temperature | °C |  |  | Min/Ave/Max
4.3 | Operating pressure | kPag |  |  | Min/Ave/Max
4.4 | pH | - |  |  | Min/Ave/Max
4.5 | Dissolved organic carbon (DOC) | mg/L |  |  | Min/Ave/Max
4.6 | Calcium (as CaCO3) | mg/L |  |  | Min/Ave/Max
4.7 | Langelier Index | - |  |  | Min/Ave/Max
4.8 | Alkalinity (as CaCO3) | mg/L |  |  | Min/Ave/Max
4.9 | Turbidity | NTU |  |  | Min/Ave/Max
4.1 | Total dissolved solids | mg/L |  |  | Min/Ave/Max
4.11 | UV transmittance at 254 nm | % |  |  | Min/Ave/Max
4.12 | Manganese | mg/L |  |  | Min/Ave/Max
4.13 | Iron | mg/L |  |  | Min/Ave/Max
4.14 | Fluoride | mg/L |  |  | Min/Ave/Max
4.15 | Free chlorine | mg/L |  |  | Min/Ave/Max
5 | System Water Quality Data
5.1 | Flow Type
5.2 | WTP Design Flow Rate | ML/d |  |  | Min/Ave/Max
5.3 | Total inflow to Lead and Lag UV units | L/s |  |  | Min/Ave/Max
5.4 | No. of UV reactors online | Qty |  |  | Min/Ave/Max
5.5 | Required Flow per UV reactor | ML/d |  |  | Min/Ave/Max
5.6 | Required Flow per UV reactor | L/s |  |  | Min/Ave/Max
5.7 | Single UV reactor maximum pressure loss | kPag |  |  | Min/Ave/Max
5.8 | Total maximum pressure drop across two UV reactors | kPag
5.9 | Minimum UV reactor flowrate | L/s
5.1 | Maximum UV reactor flowrate | L/s
5.11 | Maximum UV reactor flowrate | ML/d
5.12 | UV Reactor operating pressure | kPag
5.13 | Maximum UV reactor pressure | kPag
5.14 | Maximum UV reactor negative pressure | kPag
5.15 | UV reactor headloss curve | -
5.16 | Minimum straight pipe upstream | m
5.17 | Minimum straight pipe downstream | m
6 | Performance Requirements
6.1 | Reduced equivalent dose (RED) | mJ/cm2
6.2 | Validated UV dose (end of lamp life) | mJ/cm2
6.3 | Validation | -
6.4 | Automatic dose pacing control | -
6.5 | Guaranteed LRV at Validated Dose
6.6 | Protozoa (Cryptosporidium) | LRV
6.7 | Protozoa (Giardia) | LRV
6.8 | Bacteria (E. Coli) | LRV
6.9 | Viruses (Adenovirus) | LRV
7 | UV Reactor
7.1 | Mounting | horiz/vert
7.2 | Inlet / Outlet Connection
7.3 | Size | DN
7.4 | Flange standard | -
7.5 | Flange type | -
7.6 | Material | -
7.7 | Flange pressure rating | -
7.8 | Dimensions and Weights
7.9 | Weight of each UV reactor | kg (dry and wet)
7.1 | Overall dimension of each UV reactor | mm x mm x mm
7.11 | UV Reactor Inlet/Outlet Arrangement | -
7.12 | Orientation of outlet flange | -
8 | UV Lamps and Quartz Sleeves
8.1 | Type (e.g. low or medium pressure lamps) | -
8.2 | Model No. | -
8.3 | Manufacturer | -
8.4 | Place of Manufacture | -
8.5 | Supplier | -
8.6 | No. of UV lamps per reactor | Qty
8.7 | Total No. of UV lamps in two UV reactors | Qty
8.8 | Lamp UV radiation @ 254 nm | mJ/cm2
8.9 | Lamp power | W
8.1 | Lamp voltage | V
8.11 | Lamp current | A
8.12 | Turndown on lamp | %
8.13 | No. of lamp starts per day | No./d
8.14 | Lamp start-up time | mins |  |  | Vendor to note if cooling is requried during lamp warm-up period
8.15 | Guaranteed Lamp life - from manufacture | hours
8.16 | Lamp aging factor | -
8.17 | Lamp failure allowance | % |  |  | No. of lamps failed to still achieve validation. Supplier to advise
8.18 | Recommended contingency for lamp breaking and Hg release | -
8.19 | Quartz sleeve fouling factor | -
8.2 | Quartz sleeve transmission factor | -
8.21 | Guaranteed quartz sleeve life | Years
8.22 | Automatic cleaning system | -
8.23 | Automatic cleaning system type (electric/ pneumatic) | -
8.24 | Guaranteed automatic cleaning system life | Years
8.25 | No. of Wiper motors | Qty
8.26 | Wiper motor rating | W / V / A
8.27 | Wiper motor service factor | -
8.28 | UV reactor idle time at no flow | mins
8.29 | Lamp cable length | m
8.3 | Lamp cable details | -
8.31 | Lamp warm up time to achieve required UV dose | mins
8.32 | Recommended duration UV reactor to be turned on with UV outlet valve in close position | mins
8.33 | Cool down time required before turning on UV reactor | mins
8.34 | Individual lamp failure indicator | -
9 | UV Ballast Units
9.1 | Type | -
9.2 | Model No. | -
9.3 | Manufacturer | -
9.4 | Place of Manufacture | -
9.5 | Supplier | -
9.6 | No. of lamps per ballast | Qty
9.7 | Guaranteed ballast life | hours
9.8 | Allowable voltage variation | %
9.9 | Power factor | -
9.1 | Ballast efficiency | %
9.11 | Heat Production per unit | W
9.12 | Total heat production per two UV reactors | W
9.13 | UV ballast cabinet location | -
9.14 | Individual ballast failure indicator | -
10 | UV Reactor Temperature Sensor
10.1 | Type | -
10.2 | No. supplied per UV reactor | Qty
10.3 | Model No. | -
10.4 | Manufacturer | -
10.5 | Place of Manufacture | -
10.6 | Supplier | -
10.7 | IP rating | -
10.8 | Measurement accuracy ± | °C
10.9 | Measuring range | °C
10.1 | Signal output | -
10.11 | Guaranteed life | Years
11 | UV Reactor Intensity Sensor
11.1 | Type | -
11.2 | No. supplied per UV reactor | Qty
11.3 | Model No. | -
11.4 | Manufacturer | -
11.5 | Place of Manufacture | -
11.6 | Supplier | -
11.7 | Frequency of calibration | -
11.8 | Initial calibration standard | -
11.9 | On-going method of calibration | -
11.1 | Location of recalibration | -
11.11 | IP rating | -
11.12 | Measurement uncertainty ± | %
11.13 | Measuring range | nm
11.15 | Signal output | -
11.16 | Guaranteed life | Years |  |  | Minimum 15 years design life.
12 | UV Reactor Transmissivity Analyser
12.1 | Type | -
12.2 | No. supplied per UV reactor | Qty
12.3 | Model No. | -
12.4 | Manufacturer | -
12.5 | Place of Manufacture | -
12.6 | Supplier | -
12.7 | Measurement range | %T
12.8 | Reproducibility | %T
12.9 | Resolution | %T
12.1 | Accuracy | %T
12.11 | Response time | secs
12.12 | Enclosure IP rating | IP
12.13 | Operating temperature | °C
12.14 | Analogue Output | -
12.15 | Guaranteed life | Years |  |  | Minimum 15 years design life.
13 | UV Power Ballast Cabinets
13.1 | Type | -
13.2 | No. supplied | Qty
13.3 | Model No. | -
13.4 | Manufacturer | -
13.5 | Place of Manufacture | -
13.6 | Supplier | -
13.7 | Location | -
13.8 | Design and construction standard | - |  |  | SA Water TS 0300 and AS/NZS 3000
13.9 | Construction material | - |  |  | SA Water TS 0300
13.1 | IP Rating | IP
13.11 | Power demand | kW or KVA
13.12 | Cable entry | -
13.13 | Cooling Requirements | -
13.14 | Typical drawing layout | -
13.15 | Dimensions | mm x mm x mm
13.16 | Total weight | kg
13.17 | Surge protection | Req/ Not Req
14 | UV Control Cabinet
14.1 | Type | -
14.2 | No. supplied | Qty
14.3 | Model No. | -
14.4 | Manufacturer | -
14.5 | Place of Manufacture | -
14.6 | Supplier | -
14.7 | Location | -
14.8 | Maximum distance between UV electrical panel and UV system | -
14.9 | Design and construction standard | - |  |  | SA Water TS 0300 and AS/NZS 3000
14.1 | Construction material | - |  |  | SA Water TS 0300
14.11 | IP Rating | IP
14.12 | Power demand | kW
14.13 | Power factor | -
14.14 | Harmonic filters required | - |  |  | IEC 61000 Electromagnetic compatibility
14.15 | Cable entry | -
14.16 | Cooling Requirements | - |  |  | If not required, supplier to provide justification
14.17 | Typical drawing layout | -
14.18 | Dimensions | mm x mm x mm
14.19 | Total weight | kg
14.2 | PLC Manufacturer | -
14.21 | PLC model no. | -
14.22 | Control voltage | V |  |  | AC/DC power supplies to be provided as part of vendor scope
14.23 | Control system UPS/battery backed supply | - |  |  | As per SA Water TS 0300
14.24 | HMI manufacturer | -
14.25 | HMI Model | -
14.26 | HMI screen size | -
14.27 | HMI screen colour | -
14.28 | Interface with main plant PLC | -
14.29 | Interface hardwired control & monitoring (but not limited to) | -
14.3 | Interface communication protocol | - |  |  | Digital I/O - volt free contacts (preferred) Analog I/O - 4-20mA
14.31 | Guaranteed PLC and components life | Years
15 | Accessories
15.1 | UV reactor support frame | -
15.2 | UV reactor air bleed valve | -
15.3 | UV reactor drain valve | -
15.4 | Special tools | -
15.5 | Other
16 | Materials
16.1 | UV reactor | -
16.2 | Fasteners | -
16.3 | Quartz sleeve brushes / wipers | -
16.4 | Wiper carriage rings | -
16.5 | Wiper shaft | -
16.6 | UV reactor air ball valve | -
16.7 | UV reactor drain ball valve | -
16.8 | UV reactor support frames | -
17 | PROTECTIVE COATINGS
| UV ballast power cabinets | -
| UV control cabinet | -
| UV reactors | -
| Specification | -
EQUIPMENT LABELLING
| Label Material | -
| Information Required | -
| Fixing Method | -
MAINTANANCE ACCESS
| Front access (view front on) | mm
| Rear access | mm
| Left hand side (viewed from drive end) | mm
| Right hand side (viewed from drive end) | mm
TESTING
| Material Testing | -
| Other Approvals / Standards | -
| Quality Records | -
UV System Validation
| Validation protocol | -
| Validation test report | -
SPARE PARTS
| UV lamps | Qty
| Quartz sleeves | Qty
| O-Ring seals | Qty
| Wipers / brushes | Qty
| Wiper drive mechanism | Qty
| Electronic ballast card | Qty
| Ballast cabinet cooling fan | Qty
| UV sensor (including o-ring) | Qty
| Reference UV sensor | Qty
| PLC power supply | Qty
| PLC analogue input card | Qty
| PLC analogue output card | Qty
| PLC digital input card | Qty
| PLC digital outlet card | Qty
Other
DESIGN DOCUMENTATION
| GA & Sectional drawings (AutoCAD) | -
| P&ID's (AutoCAD) | -
| Electrical schematics (AutoCAD) | -
| Control cabinet electrical schematics | -
| Control cabinet dimensional drawing | -
| Electrical load calculation | -
| Control philosophy | -
| Operation & Maintenance Manual | -
| Commissioning plan | -
| Other (e.g., lifting option) | -
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Substation
Datasheet
| Client |  |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Kiosk Substation |  | Revision Description
Equipment No./Asset ID
Number |  | Units | Specification | Offered | Additional Comments
1 | General
1.1 | Meeting Australian Standard(s)
1.2 | Manufacturer
1.3 | Shop Drawings | Req/Not Req |  |  | Principal to review and accept prior to fabrication
1.4 | Label Schedule | Req/Not Req |  |  | Principal to review and accept prior to fabrication
1.5 | Enclosure Type
1.6 | Enclosure Class
1.7 | Enclosure Construction Material
1.8 | Degree of Protection - HV Compartment | IP
1.9 | Degree of Protection - Tx. Compartment | IP
1.1 | Degree of Protection - LV Compartment | IP
1.11 | Plinth
1.12 | Colour
1.13 | Maximum Overall Dimension (L x W x H) | mm
1.14 | Oil Containment required | %
2 | Operating Conditions
2.1 | Min Air Ambient Temperature | ºC
2.2 | Max Air Ambient Temperature | ºC
2.3 | Location
2.4 | Environment
2.5 | Humidity | %
3 | HV Switchgear - General
3.1 | Manufacturer
3.2 | Model
3.3 | Rated Voltage | kV
3.4 | Rated Current | A
3.5 | Bulk Insulation Level | kA
3.6 | Rated Fault Current | kA
3.7 | Frequency | Hz
3.8 | Module Configuration
3.9 | Insulation
3.1 | Internal Arc Classification
3.11 | Auxiliary Voltage | VDC
3.12 | Auxiliary Power Supply Make
3.13 | Auxiliary Power Supply Rating | A
3.14 | Auxiliary Power Supply Installation
4 | HV Switchgear - Cable Module
4.1 | Panel Type
4.2 | Panel Rating | A
4.3 | Voltage Presence | n/a
4.4 | Cable Connection Size | mm2
4.5 | Cable Connection Type
4.6 | Motorised Load Break Switch
4.7 | Auxiliary Contacts
5 | HV Switchgear - Circuit Breaker Module - Transformer Protection
5.1 | Panel Type
5.2 | Circuit Breaker Rating | A
5.3 | Voltage Presence
5.4 | Current Transformers
5.5 | Circuit Breaker Motorised
5.6 | Protection Relay
5.7 | Protection Relay Operating Voltage | VDC
5.8 | Cable Connection Size to Transformer | mm2
5.9 | Cable Connection Type
5.1 | Cable Connection Size | mm2
5.11 | Local Operation Selector Switch
5.12 | Local Push Buttons
5.13 | Local Indications
5.14 | Auxiliary Contacts
6 | HV Switchgear - Circuit Breaker Module - Feeder Protection
6.1 | Panel Type
6.2 | Panel Rating | A
6.3 | Voltage Presence
6.4 | Current Transformers
6.5 | Circuit Breaker Motorised
6.6 | Protection Relay
6.7 | Protection Relay Operating Voltage | VDC
6.8 | Cable Connection Type
6.9 | Cable Connection Size | mm2
6.1 | Local Operation Selector Switch
6.11 | Local Push Buttons
6.12 | Local Indications
6.13 | Auxiliary Contacts
7 | HV Switchgear - LV Compartment
7.1 | DC Control Wire Colour and Size | mm2
7.2 | CT Secondaries | mm2
7.3 | Earth Wiring | mm2
7.4 | CT Test Links
7.5 | Terminals
7.6 | Cable Markers
7.7 | Cable Terminations
7.8 | Degree of Protection | IP
8 | Transformer
8.1 | Manufacturer
8.2 | Australian Standard(s)
8.3 | Power | kVA
8.4 | Primary rated current | A
8.5 | Secondary rated current | A
8.6 | Tertiary rated current | A
8.7 | Primary rated voltage | kV (L-L)
8.8 | Secondary No Load voltage | kV (L-L)
8.9 | Tertiary No Load voltage | kV (L-L)
8.1 | Phases | No.
8.11 | Number of windings | No.
8.12 | Frequency | Hz
8.13 | Vector Group to IEC 60076.1
8.14 | Rated short time withstand current and duration
8.15 | Short circuit impedance Z1(Prim - Sec) | %
8.16 | Short circuit impedance Z1(Prim - Tert) | %
8.17 | Zero sequence impedance (Z0) Primary - Secondary | %
8.18 | Zero sequence impedance (Z0) Primary - Tertiary | %
8.19 | X/R Ratio
8.2 | Short time load current capability | %
8.21 | Maximum unbalanced load capability | %
8.22 | Tap changer Type (On load/ Off load)
8.23 | Tap changing side
8.24 | Nominal tap position | No.
8.25 | Maximum tap position | No.
8.26 | Minimum tap position | No.
8.27 | Cooling Type
8.28 | Oil Type
8.29 | Oil Temperature Indicator
8.3 | Oil Temperature Indicator Aux. Contacts
8.31 | Oil Temperature Alarm | °C
8.32 | Oil Temperature Trip | °C
8.33 | Pressure Relief Valve
8.34 | Pressure Relief Valve Aux. Contacts
8.35 | Winding Material
8.36 | Offline Tapping
8.37 | Winding Temperature Rise | °C
8.38 | Oil Temperature Rise | °C
8.39 | Name Plate
8.4 | Name Plate - Must include transformer rating at air ambient temperature | ºC
9 | LV Switchgear
9.1 | LV Switchboard Segregation
9.2 | LV Switchboard Degree of Protection
9.3 | LV Switchboard Fault Level
9.4 | LV Switchboard Enclosure
9.5 | Main Switch Type
9.6 | Main Switch Remote Operation
9.7 | Main Switch Make
9.8 | Main Switch Model
9.9 | LV Busbars details
10 | Earthing
10.1 | Australian Standard(s)
10.2 | Project Reference Drawing
10.3 | Earth Bar Details
11 | Remote Control Panel
11.1 | Project Reference Drawing
12 | Testing
12.1 | Testing Plan to be submitted |  |  |  | Prior to FAT witnessing
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300 and TS0340
Revision History
| Revision Description | Rev | Date | By | Chk

## H2S Sensor
Datasheet
| Client | SA Water |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | H2S Sensor/Analyser/Monitor (Choose one) |  | Tag No.
Number |  | Units | Specification | Offered | Additional Comments
1 | Installation and Service Conditions
1.1 | Process fluid |  | Foul Air / H2S
1.2 | Flow rate (min / norm / max) | m3/hr
1.3 | H2S (min / norm / max) | ppm
1.4 | Pressure rating (min / norm / max) | kPa
1.5 | Environmental conditions | Indoor / Outdoor | Outdoor
1.6 | Ambient temperature (min / max) | °C | -5 to 50 |  | Refer to TS0300 Section 4.1
1.7 | Humidity | % RH
1.8 | Design Life | Years | 15 |  | Refer to SAW-ENG-ODO-MUL-TSB-002 Section 3.3.1
2 | Sensor
2.1 | Manufacturer |  | Draeger
2.2 | Model no.
2.3 | Part no.
2.4 | Hazardous area classification |  | Yes
2.5 | Hazardous area certification |  | Yes
2.6 | Available range | ppm | 0-1000
2.7 | Measuring principle |  |  |  | i.e. Electro Chemical
2.8 | Measuring task |  | Continuous H2S
2.9 | Process connection - Size
2.1 | Process connection - Type
2.11 | Process connection - Material
2.12 | Sample time
2.13 | Housing - IP rating | IP |  |  | Min. IP56 - SAW-ENG-ODO-MUL-TSB-002 Section 12.3
2.14 | Housing - Material
2.15 | Housing - Mounting
2.16 | Signal cable type
2.17 | Signal cable length | m
2.18 | Integral pump | Yes / No
2.19 | Mounting position | Vertical / Horizontal
2.2 | Calibration requirements
2.21 | Maintenance requirements
2.22 | Calibration certificate | Req / Not Req
3 | Transmitter
3.1 | Manufacturer
3.2 | Accuracy | %
3.3 | Linearity | %
3.4 | Repeatability | %
3.5 | Power supply | V
3.6 | Power consumption | W
3.7 | Signal output | mA | 4-20 |  | Refer to SAW-ENG-ODO-MUL-TSB-002 Section 11.3
3.8 | Alarm Signal | Yes / No
3.9 | Operating temperature range | °C
3.1 | Electrical connection
3.11 | Available range | ppm | 0-1000
3.12 | Calibrated range | ppm
3.13 | Range setpoint | ppm
3.14 | Direct / remote electronics
3.15 | Control mode
3.16 | Response time
3.17 | Local indication |  | Yes |  | Refer to SAW-ENG-ODO-MUL-TSB-002 Section 11.3
3.18 | Calibration requirements
3.19 | Maintenance requirements
3.2 | Calibration certificate
Delivery / Lead Time
| Complete | Weeks
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Equipment shall comply with SA Water Technical Standard TS 0300
Revision History
| Revision Description | Rev | Date | By | Chk

## Battery Charger Systems
Datasheet
| Client |  |  | Project Number
| Project Title |  |  | Current Revision
| Equipment Title | Battery Charger Systems (HV Switchboard DC Supply and UPS) |  | Revision Description
Equipment No./Asset ID
Number |  | Units | Specification | Offered | Additional Comments
1 | Battery Charger Manufacturer Information
1.1 | Manufacturer
1.2 | Equipment type / Make
1.3 | Equipment number / Model
1.4 | Country of manufacture
2 | Site Conditions
2.1 | Ambient temperature (min / max) | ºC | -5/50
2.2 | Humidity | % RH | 0/90
3 | Electrical Input
3.1 | Nominal AC Voltage Input | V AC | 400
3.2 | AC Voltage Operating Range | V AC | 376 to 440
3.3 | Max Input Current (per rectifier) | A
3.4 | Power Factor (100% Load) |  | >0.99
3.5 | Nominal Input Frequency | Hz | 50
4 | Electrical Output
4.1 | Rectifier Type
4.2 | No. of Rectifiers |  | 2 (minimum) |  | Rectifier redundancy is required
4.3 | Max No. of Rectifiers
4.4 | Hot-swappable Rectifiers | Y/N | Y
4.5 | Battery Specification | Ah
4.6 | Battery Type | VRLA/Lithium | VRLA
4.7 | No. Batteries Per String
4.8 | No. of Battery Strings
4.9 | System Output Voltage | V DC
4.10 | System Output Voltage Range | V DC
4.11 | Rated Power Output (per rectifier) | kW
4.12 | Rated Current Output (per rectifier) | A
4.13 | Rated Power Output (total) | kW
4.14 | Rated Current Output (total) | A
4.15 | Efficiency (110% Load) | % | >90%
4.16 | Power Save |  | User configurable
4.17 | THD | %
4.18 | Noise and Ripple (100% Load, No Battery Connected) | %
4.19 | Cooling | Forced / Natural
5 | Battery Charger Distribution
5.1 | AC Isolation MCB
5.2 | Charger Output Isolation MCB
5.3 | Battery Isolation MCB
5.4 | DC Distribution MCB
5.5 | DC Distribution MCB Auxiliary Contacts |  | Yes
6 | Monitoring, Controls and Alarms
6.1 | Monitoring and Control |  | LCD Touchscreen
6.2 | Hardwired Alarms |  | 1. Battery over voltage; 2. Battery under voltage; 3. Supply failure; 4. Sub circuit breaker trip; 5. Charger failure; and 6. Earth fault on battery system.
6.3 | Control Voltage | V DC
6.4 | Communications
7 | Mechanical and Environmental
7.1 | Battery charger cabinet size
7.2 | Cabinet Colour
7.3 | Cabinet IP Rating
7.4 | Cabinet material |  | Mild Steel
7.5 | Cabinet Dimensions
7.6 | Battery Racking Configuration | Contained in battery charger cubicle or separate cubicle
7.7 | Battery Racking - No. Shelves
7.8 | System Weight | Kg
7.9 | Floor Loading | kPa
7.10 | Operating Temperature Range | ºC
8 | Battery Charger Options
8.1 | Battery and DC Testing Points | Y/N
8.2 | Advanced battery monitoring | Y/N
9 | DC Distribution Board
9.1 | DB cabinet size
9.2 | DB cabinet colour
9.3 | DB IP Rating
9.4 | DB cabinet material |  | Mild Steel
9.5 | No. DC Distribution MCBs
9.6 | DC Distribution MCB Size
9.7 | DC Distribution MCB Auxiliary Contacts |  | Yes
9.8 | No. changeover switches/isolators
9.9 | Changeover Switch/isolator manufacturer
9.10 | Changeover Switch/isolator equipment type/make
9.11 | Changeover Switch/isolator equipment number/model
Delivery / Lead Time
| Complete | Weeks |  |  | Maximum durations to be stated
| Spare parts minor components | Weeks
| Spare parts major components | Weeks
Notes
Battery charger systems shall comply with SA Water Technical Standard TS 0300 and TS 0340
Revision History
| Revision Description | Rev | Date | By | Chk