## Version
Version History
Version | Date | Author | Comments | Known Issues
0.1 | 2019-12-18 | G Holmes | Updated as part of TS0230 release
0.2 | 2020-04-17 | G Holmes | Updated as part of TS0260 release
1 | 2021-11-19 | G Holmes | For Release
2 | 2025-08-01 | J. Hamedi | Updated to suit TS 0230
3 | 2026-02-13 | J. Hamedi | CPEng and Lifting Lug added

## How to Use
SA Water Datasheet Template Instructions
How to complete the Datasheet:
1. Enter project information in the top rows of the datasheet tab, and revision details in the bottom rows of the datasheet tab.
2. When entering data into the datasheet, make sure that the units of the quantities entered are correct. If changes are made to the units, highlight the cell in yellow to indicate this.
3. If the Client has not completed a specification entry, please ensure that the specification of what is being offered is included in the "Offered" column.
4. If a particular specification parameter is not applicable to the offer, please enter "N/A" in the "Offered" column of that row.
Troubleshooting
Contact the SA Water Principal Mechanical/Hydraulic Engineer for any issues regarding this datasheet template.

## Gate valve
Technical Datasheet Gate Valve
| Project Number |  | Revision
| Project Title |  | Revision date
| Datasheet Title |  | Reviewed by (CPEng number)
| Datasheet reference |  | Approved by
|  |  |  | Note: | One datasheet per valve type and size
Item |  | Units | Specification | Offered | Additonal Comments
1 | General
1.01 | P&ID number/s
1.02 | Tag number/s
1.03 | Valve Type, Size & Class | (Required)
1.04 | Nominal Diameter (mm)
1.05 | Integral bypass | (Yes,size / No)
1.06 | Quantity
1.07 | Technical Specification |  | SA Water TS 0230, AS/NZS 2638.1, TS15, TS16, TS18 and this datasheet.
2 | Operating Conditions
2.01 | General
2.02 | Design Life (Years) | 25
2.27 | Total number of operations over the valve lifetime | Valve strokes
2.03 | Installation orientation | V / H
2.04 | Environment
2.05 | Location | (indoor/outdoor/in pit/buried)
2.06 | Atmospheric corrosivity category | AS4312
2.07 | Ambient Temperature | °C | 0 (min) / 50 (max)
2.08 | Process fluid properties
2.09 | Description
2.1 | Temperature | °C (min / max)
2.11 | Total Dissolved Solids (by EC) | mg/L
2.12 | Chlorides | mg/L
2.13 | pH
2.14 | Total Hardness as CaCO3 | mg/L as CaCO3
2.15 | Chlorine - Free | mg/L
2.16 | Hydraulic conditions
2.17 | Service function
2.18 | Sealing direction
2.19 | Maximum flow rate | L/s
2.2 | Maximum operating pressure, excluding surge | kPa g
2.21 | Maximum operating pressure, including surge | kPa g
2.22 | Minimum operating pressure, including surge | kPa g
2.23 | Maximum differential pressure (steady state) | kPa g
2.24 | Field hydrostatic test pressure | kPa g
2.25 | Operation
2.26 | Method of actuation
2.28 | Maximum rate of operation | Valve strokes per day
2.29 | Valve closing time | Seconds |  |  | N/A if manually operated
2.3 | Valve opening time | Seconds |  |  | N/A if manually operated
3 | Valve Details
3.01 | General
3.02 | Valve Model |  | Vendor to advise
3.03 | Country of origin |  | Vendor to advise
3.04 | Manufacturing standard |  | AS 4795.2
3.05 | Valve pressure rating | PN (bar) | Vendor to advise
3.06 | Allowable operating pressure (excluding surge) | kPa g | Vendor to advise
3.07 | Maximum allowable operating pressure (including surge) | kPa g | Vendor to advise
3.08 | Allowable site test pressure | kPa g | Vendor to advise
3.09 | Maximum differential pressure for end-of-line (free end) service | kPa g | Vendor to advise
3.1 | Published maximum operating torque (PMOT) | Nm | Vendor to advise |  | PMOT to consider worst case scenario of differential head, seating/unseating torque, and/or emergency flow. (Vendor to advise)
3.11 | Flow coefficient, Cv, fully open | L/s @ 1kPa | Vendor to advise
3.12 | Spindle arrangement | rising/non rising
3.13 | Direction of valve closure |  | Clockwise
3.14 | Position indicator | Yes / No
3.15 | Lifting provisions | AS/NZS 2638.1/2
3.24 | Lifting lug | N (axial) / N (radial) | Vendor to advise
3.16 | Extension spindle - Height from valve centreline to top of spindle | mm (or N/A if no extn spindle required)
3.17 | Minimum straight length of pipeline required upstream of valves | mm
3.18 | Minimum straight length of pipeline required downstream of valves | mm
3.19 | Air bleed valve in bonnet | Y / N
3.19 | Flanged end connections
3.2 | Flange type and description
3.21 | Bolt hole drilling pattern
3.22 | Flange sealing area surface finish
3.23 | Load limits | N (axial) / N (radial) | Vendor to advise
3.24 | Gearbox
3.25 | Manufacturer |  | Vendor to advise
3.26 | Model |  | Vendor to advise
3.27 | Type | worm / bevel / spur | Vendor to advise
3.28 | Ratio |  | Vendor to advise
3.29 | Single/Dual speed | Y / N | Vendor to advise
3.29 | Mechanical advantage |  | Vendor to advise
3.3 | Maximum allowable input torque | Nm | Vendor to advise
3.31 | Gearbox orientation |  | Vendor to advise
3.32 | Gearbox IP Rating |  | Vendor to advise
3.33 | Number of turns for full valve stroke |  | Vendor to advise
3.34 | Maximum input torque required to operate valve | Nm | Vendor to advise
3.35 | Material
3.36 | All materials to be in accordance with ASNZS2638.1/2 as a minimum |  | AS/NZS 2638.1/2
3.37 | Body |  | SGCI (DI) to AS1831 400-15
3.38 | Bonnet and seal retainer housing (where applicable) |  | SGCI (DI) to AS1831 400-15
3.39 | Body internal coating
3.4 | Body external coating |  | FBE to AS 4158 to min 300 microns thickness OR High Build 2 Pack Epoxy in accordance with SAW TS97
3.41 | Bypass fittings
3.42 | Spindle seal retainer |  | Copper alloy AS 1565 C83600
3.43 | Gate |  | SGCI (DI) to AS1831 400-15
3.44 | Gate coating
3.45 | Gate nut |  | Copper alloy AS 1565 C83600
3.46 | Seating rings |  | Copper alloy AS 1565 C83600
3.47 | Gate guides / shoes |  | Copper alloy AS 1565 C83600 |  | Gate guides and shoes to be provided and secured with fasteners as opposed to welded.
3.48 | Spindle |  | ASTM A276 Grade 431
3.49 | Spindle cap
3.5 | Fasteners |  | 316SS
3.51 | Gaskets |  | AS1646 EPDM
3.52 | O-rings |  | AS1646 NBR
3.53 | Dimensions & weight
3.54 | Flange face to face | mm | Vendor to advise
3.55 | Flange sealing face internal diameter | mm | Vendor to advise
3.56 | Total weight | kg | Vendor to advise |  | Including gearbox if applicable
3.57 | Testing, Certification and Documentation
3.58 | Testing |  | AS/NZS 2638.1/2
3.59 | Valve product certification |  | AS/NZS 2638.1/2
3.6 | Coating product certification |  | AS/NZS 4158 (for FBE) or APAS 2975P/2977P (for high build 2 pack epoxy)
3.61 | Coating repair procedure | Yes / No
3.62 | Seal test | Yes / No
3.63 | Reverse seal test for bi-directional valves | Yes / No
3.64 | Dimensioned Enginering Drawing | Yes / No
3.65 | Manufacturing Inspection and test plan (ITP) | Yes / No
3.66 | Installation, operation and maintenance manual | Yes / No
3.67 | Flow characteristic curve, Cv vs % open | Yes / No
Tenderers Details
Completed by (name)
Date
Revision History
| Revision Description | Rev | Date | By | Chk

## Butterfly Valve
Technical Datasheet Butterfly Valve
| Project Number |  | Revision
| Project Title |  | Revision date
| Datasheet Title |  | Reviewed by (CPEng number)
| Datasheet reference |  | Approved by
Item |  | Units | Specification | Offered | Additonal Comments
1 | General
1.01 | P&ID number/s | (Required)
1.02 | Tag number/s | (Required)
1.03 | Nominal Diameter | DN (mm)
1.04 | Quantity
1.05 | Technical specification |  | SA Water TS0230
2 | OPERATING CONDITIONS
2.01 | General
2.02 | Design Life | years
2.03 | Installation orientation
2.04 | Environment
2.05 | Location
2.06 | Atmospheric corrosivity category | AS 4312
2.07 | Ambient Temperature range | °C (min - max)
2.08 | Process fluid properties
2.09 | Description
2.1 | Temperature | °C (min - max)
2.11 | Total Dissolved Solids (by EC) | mg/L
2.12 | Chlorides | mg/L
2.13 | pH
2.14 | Total Hardness as CaCO3 | mg/L as CaCO3
2.15 | Chlorine - Free | mg/L
2.16 | Hydraulic Conditions
2.17 | Service function
2.18 | Sealing direction
2.19 | Maximum flow rate | L/s
2.2 | Maximum operating pressure, excluding surge | kPa g
2.21 | Maximum operating pressure, including surge | kPa g
2.22 | Minimum operating pressure, including surge | kPa g
2.23 | Maximum Differential Pressure (steady state) | kPa g
2.24 | Minimum cavitation index during continued operation |  |  |  | Refer TS230 Section 4.5.2 for calculation of cavitation index
2.25 | Minimum cavitation index during intermittent operation |  |  |  | Refer TS230 Section 4.5.2 for calculation of cavitation index
2.26 | Field hydrostatic test pressure | kPa g
2.27 | Operation
2.28 | Method of actuation
2.29 | Total number of operations over the valve lifetime | Valve strokes |  |  | From fully closed to fully open is considered one stroke
2.3 | Maximum rate of operation | Valve strokes per day
2.31 | Valve closing time | Seconds
2.32 | Valve opening time | Seconds
3 | Valve Details
3.01 | Valve Data
3.02 | Valve Model
3.03 | Country of Origin
3.04 | Manufacturing standard | AS 4795.2
3.05 | Valve pressure rating | PN (bar)
3.06 | Allowable operating pressure (excluding surge) | kPa g
3.07 | Maximum allowable operating pressure (including surge) | kPa g
3.08 | Allowable site test pressure | kPa g
3.09 | Maximum differential pressure for end-of-line (free end) service | kPa g
3.1 | Published Maximum Operating Torque (PMOT) | Nm
3.11 | Flow coefficient, Cv, fully open | L/s @ 1kPa
3.12 | Minimum allowable cavitation index for continuous operation
3.13 | Minimum allowable cavitation index for intermittent operation
3.14 | Direction of valve closure
3.15 | Body style
3.16 | Disc eccentricity
3.17 | Seal arrangement
3.18 | Seat fixing arrangement | eg, welded overlay, mechanical fixing, rolled in
3.19 | Shaft arrangement | through / stub
3.2 | Shaft to disc connection | pinned / keyed / polygon / other
3.21 | Input stop | Yes / No
3.22 | Position indicator | Yes / No
3.23 | Lifting provisions | AS 4795.2 Section 3.6
3.27 | Lifting lug | N (axial) / N (radial) | Vendor to advise
3.24 | Extension spindle - Height from valve centreline to top of spindle | mm (or N/A if no extn spindle required)
3.25 | Minimum straight length of pipeline required upstream of valve | mm
3.26 | Minimum straight length of pipeline required downstream of valve | mm
3.27 | Flanged end connections
3.28 | Flange type and description
3.29 | Bolt hole drilling pattern
3.3 | Flange sealing area surface finish
3.31 | Load limits | N (axial) / N (radial)
3.32 | Gearbox
3.33 | Manufacturer
3.34 | Model
3.35 | Type | worm / bevel / spur
3.36 | Ratio
3.37 | Mechanical advantage
3.38 | Maximum allwable input torque | Nm
3.39 | Gearbox orientation
3.4 | Gearbox IP Rating
3.41 | Number of turns for full valve stroke
3.42 | Materials
3.43 | All materials to be in accordance with AS 4795.2 as a minimum
3.44 | Body
3.45 | Body internal coating
3.46 | Body external coating
3.47 | Disc
3.48 | Disc Coating
3.49 | Seal / liner | EPDM AS 1646
3.5 | Seal retaining ring
3.51 | Seat
3.52 | Shaft
3.53 | O-rings
3.54 | Shaft bearings
3.55 | Disc-to-shaft fixing
3.56 | Fasteners (in contact with process fluid)
3.57 | Fasteners (not in contact with process fluid)
3.58 | Extension spindle
3.59 | Gearbox housing material
3.6 | Gearbox coating
3.61 | Gearbox input shaft
3.62 | Dimensions & weight
3.63 | Overall length (between sealing faces) | mm | Vendor to advise
3.64 | Flange sealing face internal diameter | mm | Vendor to advise
3.65 | Flange sealing face outside diameter | mm | Vendor to advise
3.66 | Maximum allowable internal diameter of mating flange face to ensure successful seal | mm | Vendor to advise
3.67 | Flange thickness | mm | Vendor to advise
3.68 | Shaft diameter at smallest cross-sectional area | mm | Vendor to advise
3.69 | Dimension across disc at the plane of the flange face when disc in fully open position | mm | Vendor to advise
3.7 | Total weight (incl gearbox) | kg | Vendor to advise
3.71 | Testing, certification and documentation
3.72 | Testing |  | AS 4795.2
3.73 | Free end test | Yes / No
3.74 | Valve product certification |  | ISO system 5 product certification to AS4795.2
3.75 | Coating product certification |  | AS/NZS 4158 (for FBE)
3.76 | Drinking water certification | Yes / No
3.77 | Inspection and Test Plan (ITP) | Yes / No
3.78 | Dimensioned Engineering Drawing | Yes / No
3.79 | Installation, operation and maintenance manual | Yes / No
3.8 | Flow characteristic curve, Cv vs % open | Yes / No |  |  | To be supplied with tender for technical evaluation. Units of Cv must be stated.
Tenderers Details
Completed by (name)
Date
Revision History
| Revision Description | Rev | Date | By | Chk

## Flowmeter
Technical Datasheet Flowmeter
| Project Number |  | Revision
| Project Title |  | Prepared by
| Datasheet Title |  | Reviewed by (CPEng number)
| Datasheet reference |  | Approved by
Item |  | Units | Data / Specification | Offered | Additonal Comments
1 | General
1.01 | Tag number
1.02 | Service Description
1.03 | P&ID Number
1.04 | Equipment / Line Number
1.05 | Nominal Diameter | DN (mm)
1.06 | Pipe Material
1.07 | Quantity
1.08 | Technical Specification | SA Water TS0260
2 | Operating Conditions
2.01 | General
2.02 | Design Life | years
2.03 | Installation Orientation
2.04 | Environment
2.05 | Location | Indoor/Outdoor/In-pit/Buried
2.06 | Atmospheric Corrosivity Category | AS2312
2.07 | Ambient Temperature | °C
2.08 | Humidity | % RH
2.09 | Hazardous Area Classification |  |  |  | i.e. Zone, Gas Group/Dust Group, Temperature Class
2.1 | Process fluid properties
2.11 | Fluid Type Description |  | ` |  | Potable, non-potable, raw water, wastewater, etc
2.12 | Total Dissolved Solids (by EC) | mg/L
2.13 | Solids Content | % by Wt.
2.14 | Solids Size | mm
2.15 | Conductivity | µS/cm (min - max)
2.16 | Turbidity | NTU
2.17 | Temperature | °C (min / max)
2.18 | Density | kg/m³
2.19 | Viscosity | cP
2.2 | Chlorides | mg/L
2.21 | pH
2.22 | Total Hardness as CaCO3 | mg/L as CaCO3
2.23 | Chlorine - Total | mg/L
2.24 | Monochloramine | mg/L
2.25 | Chlorine - Free | mg/L
2.26 | Hydraulic conditions
2.27 | Flow Direction | uni / bi directional
2.28 | Flow Rate (min) | L/s
2.29 | Flow Rate (max) | L/s
2.3 | Flow Rate (ave) / (nominal) | L/s
2.31 | Flow Velocity (min / norm / max) | m/s
2.32 | Maximum Operating Pressure (excluding surge) | kPa g
2.33 | Maximum Operating Pressure (including surge) | kPa g
2.34 | Minimum Operating Pressure (including surge) | kPa g |  |  | Vendors shall confirm the nominated flowmeter can operate without fault with pressure variations whereby vacuum pressure can form for a short period of time.
2.35 | Static Pressure (no flow) | kPa g
2.36 | Design Pressure | kPa g
2.37 | Field Hydrostatic test pressure | kPa g
3 | Flowmeter Details
3.01 | General
3.02 | Manufacturer
3.03 | Model Number
3.04 | Country of Origin
3.05 | Manufacturing Standard
3.06 | IP Rating
3.07 | Available Range | TBC by Designer
3.08 | Measuring Principle |  |  |  | i.e. Magnetic/Thermal Mass/Ultrasonic/DP/Coriolis etc.
3.09 | Measuring Task
3.1 | Pressure Rating | PN (bar)
3.11 | Allowable Operating Pressure (excluding surge) | kPa g
3.12 | Maximum Allowable Operating Pressure (including surge) | kPa g
3.13 | Allowable Site Test Pressure | kPa g
| Headloss across flowmeter at maximum flow | kPa g
3.14 | Minimum straight length of pipeline required upstream of valves/pipe direction changes | mm |  |  | i.e. Provide Any Existing Restriction Details Here
3.15 | Minimum straight length of pipeline required downstream of valves/pipe direction changes | mm |  |  | i.e. Provide Any Existing Restriction Details Here
3.16 | Flanged end connections
3.17 | Flange Face Type | O-ring / raised face / flat face
3.18 | Bolt Hole Drilling Pattern | AS4087
3.19 | Flange Sealing Area Surface Finish | Coated / Gramophone
3.2 | Flange Load Limits | N (axial) / N (radial)
3.21 | Lifting lug | N (axial) / N (radial) | Vendor to advise
3.22 | Transmitter
3.23 | Accuracy | %
3.24 | Linearity | %
3.25 | Repeatability | %
3.26 | Power Supply | VAC
3.27 | Power Consumption | W
3.28 | Operating Temperature Range | °C
3.29 | Available Range | L/s
3.3 | Calibrated Range | L/s
3.31 | Range Setpoint | L/s
3.32 | Response Time
3.33 | Transmitter Mounting | Integral / Remote
3.34 | Local Indication |  |  |  | i.e. LCD Display
3.35 | IP Rating
3.36 | Signal Output | mA |  |  | i.e. With Pulse Output for Totaliser
3.37 | Totalizer | Yes / No
3.38 | Alarm Signal | Yes / No |  |  | i.e. Via Comms
3.39 | Empty Pipe Detection | Yes / No |  |  | i.e. Via Comms
3.4 | Communications Interfaces Available |  |  |  | i.e. Modbus, Ethernet IP
3.41 | Electrical Connections (Type, Quantity) |  |  |  | i.e. M20
3.42 | Cable Type Between Meter & Transmitter |  |  |  | i.e. For Specific Vendor Supplied Cabling
3.43 | Cable Length Between Meter & Transmitter | m |  |  | i.e. For Specific Vendor Supplied Cabling
3.44 | Cable Type / Length Limitations / Requirements Between Transmitter and Control Systems |  |  |  | i.e. For Ethernet Systems
3.45 | Materials of Construction
3.46 | Body
3.47 | Liner
3.48 | Tube/Meter Casing
3.49 | Flanges
3.5 | Electrode
3.51 | Electronics Housing
3.52 | Testing, Certification & Documentation
3.53 | Flowmeter Product Certification | Yes
3.54 | Hazardous Area Ceritification | Yes / No |  |  | i.e. IECEx, ANZEx
3.55 | Hazardous Area Protection Technique Data | Yes / No |  |  | i.e. Ex d, Ex ia etc.
3.56 | Coating Product Certification
3.57 | Calibration Certification / Requirements | Yes / No |  |  | i.e. Vendor to Advise Specifics
3.58 | Coating Repair Procedure | Yes / No
3.59 | Dimensioned Enginering Drawing | Yes / No
3.6 | Manufacturing Inspection and Test Plan (ITP) | Yes / No
3.61 | Installation, Operation and Maintenance Manual | Yes / No
3.62 | Dimensions & weight
3.63 | Flange Face to Face | mm
3.64 | Flange Sealing Face Internal Diameter | mm
3.65 | Total Weight | kg
3.66 | Delivery / Lead Time
3.67 | Complete | Weeks
3.68 | Spare Parts - Minor Components | Weeks
3.69 | Spare Parts - Major Components | Weeks
3.7 | Notes / Additional Comments / Options
3.71
4 | Tenderers Details
4.01 | Completed by (name)
4.02 | Date
5 | Installation Details
Note - insert drawings, photos, etc. to inform tenderer of installation details.
Revision History
| Revision Description | Rev | Date | By | Chk

## Valve FAT testing observation
Valve Inspection Checksheet
GENERAL
Project |  | SA Water project ref.
Valve supplier |  | Date of inspection
VALVE IDENTIFICATION
Serial number |  | Nominal diameter (mm)
Valve type |  | Pressure rating (bar)
MARKING
Marking |  | Comment
Manufacturer | ☐
Nominal size (DN) | ☐
Year of Manufacture | ☐
Pressure Class (PN) | ☐
Flow direction arrow | ☐
Manufacturing Standard | ☐
Serial number | ☐
Gear ratio | ☐
Spindle cap direction of closure | ☐
Note, these are the marking requirements of AS 4795.2. Marking requirements may vary depending on the manufacturing standard.
VISUAL INSPECTION
Item | Satisfactory Yes No N/A | Comment
Position indicator | ☐ ☐ ☐
Gearbox orientation | ☐ ☐ ☐
Extension spindle | ☐ ☐ ☐
Actuator | ☐ ☐ ☐
Flange sealing face | ☐ ☐ ☐
Internal surfaces free of sharp protrusions | ☐ ☐ ☐
Coatings | ☐ ☐ ☐
DIMENSIONAL CHECK
Item | Specification | Required | Tolerance | Measured
Face-to-face length
Flange thickness
Bolt pitch circle diameter | AS/NZS 4087 |  | M12 – M24: +/- 1.5
≥ M27: +/- 2.0
Number of bolt holes | AS/NZS 4087 |  | 0
Bolt hole diameter | AS/NZS 4087 |  | +1.5, -0.5
Flanges for use with gaskets:
Flange sealing face internal diameter
Flange sealing face outside diameter
Flanges for use with o-rings:
O-ring groove depth | AS/NZS 4087 | 6 | +/- 0.5
O-ring groove width | AS/NZS 4087 | 15 | +/- 0.5
Flange flatness
Flange 1 | AS/NZS 4087 | Flat | ≤ DN250: +/- 0.2
> DN250: +/- 0.5
Flange 2 | AS/NZS 4087 | Flat | ≤ DN250: +/- 0.2
> DN250: +/- 0.5
COMMENTS
INSPECTOR DETAILS
| Name | Signature | Date
Inspected by

## Lists (hidden)
Tables for drop down lists
Location
Buried
Indoors
Outdoors
Within pit/chamber
Atmospheric corrosivity category
C1 very low
C3 low
C3 medium
C4 high
C5 very high
Sealing direction
Bi-directional sealing
Single directional sealing
Method of actuation
Manual - Handwheel
Manual - Lever
Manual - Spindle cap
Electric actuator
Pneumatic actuator
Body style
Wafer
Lugged
Double flanged
Disc eccentricity
Concentric
Double offset
Single offset
Triple offset
Vendor to advise
Seal arrangement
Seal in body
Seal on body
Seal on disc
Flange face type
Flat face
O-ring groove
Raised face
Yes/No
No
Yes